## Data sheet
Water Water heat pump unit |  | Luc, this data sheet will need completing as the project develops
Nominal heat output | 2 kW
Compressor type | Rotary
Model | L'unite Hermetique RK5480C
Refrigerant | R290 Propane ( Calor Care 40)
Power input Maximum | 680 watts
Maximum run current | 3 Amps
Condenser | Plate, stainless, copper-brazed
Evaporator | Plate, stainless, copper-brazed
Expansion valve | Thermostatic
Source temperature range | -5 to +10°C
Source fluid | glycol
Flow rate |  | 0.1666 | lit/sec
Source pump
Hot water range | +25 to 50°C
Water flow rate | flow rate | 0.095238 | lit/sec
Heating pump | Probably Grundfos Alpha-II 15-60

## Source
GROUND LOOP SIZING | [9 empty] | Comparing pressure drops, water and glycol
heat pump size | 2 | kW | [7 empty] | water | 2.5° | 23.88 | 100%
Extracted heat from source | 1.8 | kW | [8 empty] | 22.5° | 22.72 | 95.14%
[11 empty] | 52.5° | 21.88 | 91.62%
typical | 5 | kw | Figures from Stiebel Eltron | [6 empty] | glycol 35% | 2.5° | 37.17 | 155.7%
100m loops | 4 | off | [7 empty] | glycol 20% | 2.5° | 29.45 | 123.3%
rule of thumb | 2 | kw | [7 empty] | 20% glycol causes pressure drop of about 1.25 times
| 2 | loops
[10 empty] | Specific heat of water |  |  | 4.2
EXAMPLE 1, typical sizing for a 2kW heat pump. 2 x 100m loops of 25mm o.d. | [9 empty] | Specific heat of 20% glycol |  |  | 3.8
Heat transfer (evaporator) | 1.8 | kW |  |  |  |  | 24
Specific heat Glycol | 3.8 | kj/kg °C |  |  |  |  | 3.8
temperature drop | 3 | [5 empty] | 3
flow rate | 0.15789 | lit/sec | lit/hr | lit/min |  |  | 2.1053
flow rate | 0.56842 | m³/h | 568.4211 | 9.4737
flow per loop | 0.28421 | m³/h | 284.2105 | 4.7368
20% glycol
Length of pipe: | 100 | m | Ext Dia: | 25 | mm | Wall Thickness: | 2.3 | mm | Flow rate | 5 | l/min | 6381.5593 | Pa | 7976.9491
[12 empty] | 0.063816 | Bar | 0.079769
So, if 2 loops, then pressure drop is only 1 m head max. This is perfect. But pipe are a bit small | [11 empty] | 0.63816 | M head | 0.79769
[12 empty] | 6.3816 | kPa | 7.9769
EXAMPLE 2, 2 x loops of 150m | [13 empty] | 20% glycol
Length of pipe: | 150 | m | Ext Dia: | 25 | mm | Wall Thickness: | 2.3 | mm | Flow rate | 5 | l/min | 9572.3389 | Pa | 11965.4237
[12 empty] | 0.095723 | Bar | 0.11965
Pressure starting to get high! | [11 empty] | 0.95723 | M head | 1.1965
[12 empty] | 9.5723 | kPa | 11.9654
EXAMPLE 3, Alternative is to go for 3 x 100m. This will give less pump power, but 3 x manifold is much harder than 2 x manifold.
Heat transfer (evaporator) | 1.8 | kW
Specific heat Glycol | 3.8 | kj/kg °C |  | (20% ethylene glycol)
temperature drop | 3 | K
flow rate | 0.15789 | lit/sec | lit/sec | lit/min
flow rate | 0.56842 | m³/h | 568.4211 | 9.4737
flow per loop | 0.18947 | m³/h | 189.4737 | 3.1579
20% glycol
Length of pipe: | 100 | m | Ext Dia: | 25 | mm | Wall Thickness: | 2.3 | mm | Flow rate | 3.333 | l/min | 3164.553 | Pa | 3955.6913
[12 empty] | 0.031646 | Bar | 0.039557
Bordering on mixed flow, not turbulent! However, we can increse flow rate a little since pressure drop is so low | [11 empty] | 0.31646 | M head | 0.39557
[12 empty] | 3.1646 | kPa | 3.9557
EXAMPLE 4, try one long length of 32mm
20% glycol
Length of pipe: | 250 | m | Ext Dia: | 32 | mm | Wall Thickness: | 3 | mm | Flow rate | 10 | l/min | 16668.861 | Pa | 20836.0763
[12 empty] | 0.16669 | Bar | 0.20836
Pressure too high!!! | [11 empty] | 1.6669 | M head | 2.0836
[12 empty] | 16.6689 | kPa | 20.8361
GLYCOL QUANTITY | Ian Taylor |  |  | Litres/m | Enter pipe length | Volume
| pipe dia | 25mm | 20.25 | 0.3221 | 300 | 96.6312
| bore | 32mm | 25.75 | 0.52084 |  | 0
|  | 40mm | 32 | 0.80435 |  | 0
|  | 50mm | 40 | 1.2568 |  | 0
|  | 63mm | 50 | 1.9638 |  | 0
|  | volume in heat pump |  |  |  | 6
[5 empty] | TOTAL VOLUME | 102.6312
|  |  |  | glycol concentration |  | 20%
[5 empty] | Glycol content | 20.5262

## TAU
Data taken from similar heatexchanger using TAU software.
Evaporator
heat | liquid R22 |  | glycol 20%
|  |  | inlet | outlet | flow | Plates |  | Evap temp | dt evap-water out
kW | °C |  | °C | °C | kg/sec | no. | Kpa | °C
1.7 | 40 |  | 5 | 1 | 0.109 | 10 | 3.65 | -1.4 | 2.4
1.7 | 40 |  | 5 | 1 | 0.109 | 14 | 2.12 | -1 | 2
1.7 | 40 |  | 5 | 1 | 0.109 | 20 | 1.22 | -0.8 | 1.8
Condenser
heat | R22 in | R22 out | Water
|  |  | inlet | outlet | flow | Plates |  | Cond temp | dt cond-water out
kW | °C |  | °C | °C | kg/sec | no. | Kpa | °C
2 | 100 | 43 | 42 | 47 |  | 10 | 5.15 | 48.1 | 1.1
2 | 100 | 43 | 42 | 47 |  | 14 | 2.78 | 47.6 | 0.6
2 | 100 | 43 | 42 | 47 |  | 20 | 1.46 | 47.1 | 0.1
Reasons to fit smaller evaporator
1 | low velocity rising within evaporator, could lead to flooded evaporator, hence more refrigerant needed.
2 | less refrigerant quantity in system
3
Reasons why not to use small evaporator
sucion pressure significantly lower- hence lower COP
Advantages of a bigger condenser
1 | the condeser could act as a receiver, and not loose performance. I.e. if the system is over-charged, the condensing pressure will not rise much.
CONCLUSION, use 12 plate evaportaor and 16 plate condenser
EVAPORATOR
Extrapolation from 10,14 and 20 plates to 12 and 14 plates
plates | evap | [11 empty] | difference
10 | -1.4 | [9 empty] | 12 plate | -1.15
14 | -1 | [9 empty] | 16 plate | -0.9 | 0.25
20 | -0.8
Condenser
Extrapolation from 10,14 and 20 plates to 12 and 14 plates
plates | cond.
10 | 48.1 | [11 empty] | difference
14 | 47.6 | [9 empty] | 12 plate | 47.8
20 | 47.1 | [9 empty] | 16 plate | 47.4 | 0.4
the advantage of using the bigger heatehanger on condenser saves (theoretically) about 1/2 °
the advantage of using the bigger heatehanger on evaporator saves (theoretically) about 1/4 °
Looking at GEA selection
Evaporator
heat | liquid R22 |  | glycol 20%
|  |  | inlet | outlet | flow | Plates |  | Evap temp | dt evap-water out
kW | °C |  | °C | °C | kg/sec | no. | Kpa | °C
7 | 40 |  | 2 | -1.5 | 0.514 | 44 | 8.7 | -4 | 2.5
1.7 | [5 empty] | 10.6857 |  |  |  | This is equivalent to 10 plate
Condenser
heat | R22 in | R22 out | Water
|  |  | inlet | outlet | flow | Plates |  | Cond temp | dt cond-water out
kW | °C |  | °C | °C | kg/sec | no. | Kpa | °C
9 | 100 |  | 43 | 50 |  | 40 | 3.1 | 51 | 1
2 | [5 empty] | 8.8889 |  |  |  | This is equivalent to 9 plate

## plate HE
This sheet shows data for the heatexchagers to be used on the 2kW prototype | [7 empty] | 0.48 | 16 | 48
|  |  |  | Opyion 1 | Option 2 |  |  | 0.149 | 4.9667 | 6.4 | 8
|  |  | Clivet | 2kW | 2kW |  |  | 0.105 | 3.5 | 3.49
|  |  | WRHH31 | prototype | prototype
|  |  | Existing |  |  |  |  | 0.18 | 8.2 | 15
Evap |  |  | 16 plate | 16 plate | 16 plate |  |  | 0.149 | 6.7878 | 10.77 | 13.4625
Kw (cond) |  |  | 9 | 2.2 | 2.2 |  |  | 0.105 | 4.7833 | 5.93
Kw (in) |  |  | 2.2 | 0.5 | 0.5
kW (evap |  |  | 6.8 | 1.7 |  |  |  | 16-plate Evap 12-plate condenser | 12-plate evap, 16-plate condenser
COP |  |  | 4.0909 | 4.4 | 4.4 |  | Cond | 5.93 | 3.49
flow m³/h | [6 empty] | evap (water) | 8 | 10.7
flow lit/sec |  |  | 0.48 | 0.14912 | 0.10476 |  | Evap, 20% glycol | 10 | 13.375
TD |  |  | 3.373 | 3 | 5
PD hpa |  |  | 480 | 80 | 34.9
m(h) |  |  | 4.8 | 0.8 | 0.349 |  | by extrapolating original spec, we arrive at a pressure drop within this evaporator of 8.2 kPa
KPa |  |  | 48 | 8 | 3.49
Condenser |  |  | 12 plate | 12 plate | 12 plate
Kw (cond) |  |  | 9 | 2.2 | 1.7
flow m³/h
flow lit/sec |  |  | 0.18 | 0.10476 | 0.14912
TD |  |  | 11.9048 | 5 | 3
PD hpa |  |  | 150 | 59.3 | 107 |  | If the larger heatexchanger is used as the evaporator, then the pressure drop is likely to be 1.5m with water! This is getting high!
m(h) |  |  | 1.5 | 0.593 | 1.07
KPa |  |  | 15 | 5.93 | 10.7
[8 empty] | Source, glycol circuit |  |  |  | Heated water circuit
Notes | [7 empty] | Heat transfer (condenser) | 1.7 | kW |  | Heat transfer (condenser) | 2.2 | kW
Pressure drop in underfloor pipe is high, therefore condesner drop should be as low as possible, option 2 therefore better. | [7 empty] | Specific heat water | 3.8 | kj/kg °C |  | Specific heat water | 4.2 | kj/kg °C
Source could tollerate 1.3m head easily, especially since source pipework pressure drop is low. Either option OK | [7 empty] | temperature drop | 3 |  |  | temperature drop | 5
Possible refrigerant problems with a big evaporator, possibly flooding and oil-return issues. Option 2 better | [7 empty] | flow rate | 0.14912 | lit/sec |  | flow rate | 0.10476 | lit/sec
Small evaporator will cause bigger DT, but should be acceptable. | [8 empty] | 8.9474 | lit/min |  |  | 6.2857 | lit/min
Condenser would prefer a larger area to keep condensing low, Option 2 better. | [8 empty] | 0.53684 | m³/h |  |  | 0.37714 | m³/h
[8 empty] | (These are minimum requirements) |  |  |  | (These are minimum requirements)
Original data from plate heatexchangers
| Stiebel | Stiebel | Clivet |  | re- done 2006 | Stiebel | Stiebel |  |  |  | bar | 1
| WPF7 | WPF7 | WRHH31 | SWEP | IDEAL | WPF10 | WPWE8 |  |  |  | m (h) | 10
| Evap | 20% glycol | Existing | Evap | as first column | Evap | Evap |  |  |  | kPa | 100
Evap | 20? Plates |  | 18 plate | B25x20H/1P | [6 empty] | hPa | 1000
Kw (cond) | 7.8 | 7.8 | 9 |  |  | 9.9 | 8.3
Kw (in) | 1.78 | 1.78 | 2.2 |  |  | 2.2 | 2
kW (evap | 6.02 | 6.02 | 6.8 | 6 | 7 | 7.7 | 6.3
COP | 4.382 | 4.382 | 4.0909 |  |  | 4.5 | 4.15
flow m³/h | 2.1 | 1.9 |  |  |  | 2.6 | 1.9 |  |  |  | The big one
flow lit/sec | 0.58333 | 0.52778 | 0.48 | 0.396 | 0.5 | 0.72222 | 0.52778 |  |  |  | BHE maunufacturing, Alfa Laval
TD | 2.4571 | 3.0017 | 3.373 | 3.6075 | 3.3333 | 2.5385 | 2.8421 |  |  |  | Article 43020, type CB76-30L man. No. 16792296 15/06/2004
PD hpa | 100 | 100 | 480 | 166 |  | 110 | 169
m(h) | 1 | 1 | 4.8 |  |  | 1.1 | 1.69
KPa | 10 | 10 | 48 | 50 | 10 | 11 | 16.9
|  |  |  | SWEP | ideal
Condenser | 30? Plates |  | 14 plate | B15Hx 20/1P-SC-S
Kw (cond) | 7.8 |  | 9 | 8 | 9 | 9.9 | 8.3
flow m³/h | 0.8 |  |  |  |  | 1.1 | 1
flow lit/sec | 0.22222 |  | 0.18 | 0.38 | 0.3 | 0.30556 | 0.27778
TD | 8.3571 |  | 11.9048 | 5.0125 | 7.1429 | 7.7143 | 7.1143
PD hpa | 180 |  | 150 | 290 |  | 180 | 117
m(h) | 1.8 |  | 1.5 | 2.9 |  | 1.8 | 1.2
KPa | 18 |  | 15 | 29 | 18 | 18 | 12
Evaporator, (20% glycol) capacity 6kW flowrate 0.36 lit/sec ( 1.3 m³/h.) pressure drop ? around 100 hpa ? Condenser capacity 8kW flowrate 0.38 lit/sec (1.37m³/h ) pressure drop ? max 200 hpa ? Refrigerant is Propane R290
Note on D49: John Cantor: from data, too high, pump only 40kPa total
Note on D40: John Cantor: guessed at 35/0 actual 11.4 with bad he,s at 12/7-15/30
Note on D36: John Cantor: Existing heat pump
Note on D7: John Cantor: guessed at 35/0 actual 11.4 with bad he,s at 12/7-15/30
Note on D16: John Cantor: from data, too high, pump only 40kPa total

## pressure-flow calcs
1) | [8 empty] | Below is heat-flowrate calc.
3.5kW | heat output
5°C temp. Diff.
flow of 0.16 lit/sec |  |  | 0.16 | [5 empty] | ideal |  | Calorex minimum
|  |  | 9.6 | lit/min | this is ideal |  |  |  | 3.5 | kW | 3.5 | kW
ideally a calorex 3.5 would like 10 litres/min | [8 empty] | 5 | dt | 6.8 | dt
Calorex state a minimum flow of 7.5 lit/min | [8 empty] | 10 | Litres/min | 7.3529 | Litres/min
[9 empty] | 0.16667 | litres/sec | 0.12255 | litres/sec
2) |  | 16mm pipe
For 120m loop of 16mm o.d. pipe the pressure flow equation gives | [8 empty] | 3.5 | kW
3.5 | kW | [7 empty] | 14 | dt | 14° dt is far too much
5 | m head | This is the maximum realistic pressure from a domestic pump on speed 3 | [6 empty] | 3.5714 | Litres/min
3.5 | lit min | This is resulting flow with normal pump at top speed | [6 empty] | 0.059524 | litres/sec
3) |  | 15mm pipe
For 120m loop of 15mm o.d. pipe the pressure flow equation gives the following:- | [8 empty] | 3.5 | kW
3.5 | kW | [7 empty] | 18 | dt
5 | m head | [7 empty] | 2.7778 | Litres/min
2.75 | lit min | This is resulting flow with normal pump at top speed | [6 empty] | 0.046296 | litres/sec
4)
Richard Jones example
5 loops means that flowrate is dividede by 5
heat pump requires |  | 10 | lit/min
|  | 5 | number of loops
|  | 2 | lit/min per loop
For 100m loop of 16mm o.d. pipe the pressure flow equation gives the following:-
0.7 | kW | per loop
2 | lit /min required
1.6 | m head | PRESSURE DROP MUCH MUCH LOWER |  |  |  |  | pump speed 2 should be plenty
The pressure is related to a ² law, so reducung the flow reduces pump pressure dramatically.
5)
Maximum flow that can be forced down a 16mm pipe (120m long) using a normal pump | [8 empty] | 2 | kW
3.5 | lit/min | [7 empty] | 8 | dt
of about 2kW is put in, then dt is about 8°. | [8 empty] | 3.5714 | Litres/min
[9 empty] | 0.059524 | litres/sec
This means that you would always need to spill 1.5kW to the house.
This does not allow for any unknowns/ margins of safety
6) use 2 pumps to force it around!
For 120m loop of 16mm o.d. pipe the pressure flow equation gives | [8 empty] | 3.5 | kW
3.5 | kW | [7 empty] | 9.5 | dt | 9.5° dt is still too much
10 | m head | This is the maximum realistic pressure from TWO domestic pumps, speed 3 | [6 empty] | 5.2632 | Litres/min
5.2 | lit min | This is resulting flow with 2 normal pumps at top speed | [6 empty] | 0.087719 | litres/sec
| Length of pipe: | 120 | m | Ext Dia: | 16 | mm | Wall Thickness: |  | 2 | mm | Flow rate | 3.25 | l/min | 44746.813 | Pa
[8 empty] | Int Diameter: | 12 | mm |  | 0.00052 | kg/s | 0.44747 | Bar
[14 empty] | 4.4747 | M head
3.25 lit sec is the most that will flow down the 16mm pipe. | [13 empty] | 44.7468 | kPa
Heat transfer (condenser) | 1.2 | kW |  | a 2kW heat pump would balance at 9k if this loop only!
Specific heat water | 4.2 | kj/kg °C |  | we can dissipate about 1.2kW with a dt of 5k
temperature drop | 5
flow rate | 0.057143 | lit/sec
| 3.4286 | lit/min
flow rate | 0.20571 | m³/h

## calcs
The main house
room | 60 | m²
watts/m² | 50
heat (KW) | 3 | kW
spacing | 200
pipes per sqm | 5 | m
total pipe | 300 | m
each loop | 100 | m
[8 empty] | flow per loop |  | pressure if 15mm | pressure if 16mm
| m³/hr | gal/ min | lit/sec | Kwatts | lit/sec. | tem diff |  | lit/sec | m³/h
| 0.56 | 2.0496 | 0.1568 | 6 | 0.1568 | 9.1108 | this is for 3 loops | 0.052267 | 0.18667 | 4.9m | 3.11m
| m³/hr | gal/ min | lit/sec | Kwatts | lit/sec. | tem diff
| 0.24 | 0.8784 | 0.0672 | 6 | 0.0672 | 21.2585 | one loop | 0.0672 | 0.24 | 7.5m | 4.85m
The flow rate has been calculated using ; kW = lit/sec x 4.2 x temp diff.
i.e. If we are dumping 6kW in and dt is 9, we must have about .16 lit/sec flow.
now looking at pressures, it seems apparent that the pipe usd is 16mm od, probably 2.3mm wall ( however, it could be 15mm thin wall??
Anyhow, the pressures and flows seem resonable.
What we really need is to input a realistic amount into the floor over a longer period so we could tell the actual flow and return when you have say
6kW equates to 100w/m², but we want to input about 50w/m². This is in line with low-energy buildings (you would probably use less)
i.e. 3kW would be about right
Therefore, a 1hr on, 1 hr off test over say 12 hours would really tell us what would happen if you fitted a heat pump, and worked it hard in winter
However, the first test seems to proove that the floor does not budge much over 1 hour, so it is acting as a good buffer. It has a good thermal mass.
Heat transfer (condenser) | 2 | kW
Specific heat water | 4.2 | kj/kg °C
temperature drop | 5
flow rate | 0.095238 | lit/sec
flow rate | 0.34286 | m³/h

## trimmed data
Date | Time | boiler flow (out) | boiler return (in) | manifold (in) return to boiler | manifold to floor (out)
2009-05-28 | 11:51 | 16.5 | 16.5 | 17 | 17
2009-05-28 | 11:54 | 16 | 16 | 16.5 | 16.5 | 0
2009-05-28 | 11:57 | 23.5 | 16 | 16.5 | 24.5 | 7.5
2009-05-28 | 12:00 | 25 | 16.5 | 17 | 26 | 8.5
2009-05-28 | 12:03 | 25.5 | 17 | 17.5 | 27 | 8.5
2009-05-28 | 12:06 | 26.5 | 17.5 | 18 | 27.5 | 9
2009-05-28 | 12:09 | 27 | 18 | 18.5 | 28 | 9
2009-05-28 | 12:12 | 27 | 18.5 | 19 | 28.5 | 8.5
2009-05-28 | 12:15 | 27.5 | 18.5 | 19 | 28.5 | 9
2009-05-28 | 12:18 | 27.5 | 19 | 19.5 | 29 | 8.5
2009-05-28 | 12:21 | 28 | 19 | 19.5 | 29 | 9
2009-05-28 | 12:24 | 28 | 19 | 19.5 | 29 | 9
2009-05-28 | 12:27 | 28.5 | 19.5 | 20 | 29.5 | 9
2009-05-28 | 12:30 | 28.5 | 19.5 | 20 | 29.5 | 9
2009-05-28 | 12:33 | 28.5 | 19.5 | 20 | 29.5 | 9
2009-05-28 | 12:36 | 28.5 | 20 | 20 | 29.5 | 8.5
2009-05-28 | 12:39 | 29 | 20 | 20.5 | 30 | 9
2009-05-28 | 12:42 | 29 | 20 | 20.5 | 30 | 9
2009-05-28 | 12:45 | 29 | 20 | 20.5 | 30 | 9
2009-05-28 | 12:48 | 29 | 20 | 20.5 | 30.5 | 9
2009-05-28 | 12:51 | 29.5 | 20.5 | 21 | 30.5 | 9
2009-05-28 | 12:54 | 29.5 | 20.5 | 21 | 30.5 | 9
2009-05-28 | 12:57 | 29.5 | 20.5 | 21 | 30.5 | 9
2009-05-28 | 13:00 | 29.5 | 20.5 | 21 | 31 | 9
2009-05-28 | 13:03 | 30 | 21 | 21 | 31 | 9
2009-05-28 | 13:06 | 31 | 21 | 21.5 | 31 | 10
2009-05-28 | 13:09 | 31 | 22 | 21.5 | 30.5
2009-05-28
2009-05-29 | 5:48
2009-05-29 | 5:51 | 19 | 17 | 17 | 17
2009-05-29 | 5:54 | 19 | 17 | 17 | 17
2009-05-29 | 5:57 | 19 | 17 | 17 | 17 | 2
2009-05-29 | 6:00 | 17.5 | 16.5 | 17 | 17.5 | 1
2009-05-29 | 6:03 | 33 | 16.5 | 17 | 32 | 16.5
2009-05-29 | 6:06 | 38.5 | 17.5 | 18.5 | 40 | 21
2009-05-29 | 6:09 | 42 | 20.5 | 21.5 | 44 | 21.5
2009-05-29 | 6:12 | 44.5 | 22.5 | 23.5 | 46.5 | 22
2009-05-29 | 6:15 | 43.5 | 24 | 25 | 43.5 | 19.5
2009-05-29 | 6:18 | 40.5 | 25 | 25.5 | 44 | 15.5
2009-05-29 | 6:21 | 43.5 | 25 | 26 | 44.5 | 18.5
2009-05-29 | 6:24 | 42 | 25.5 | 26.5 | 42.5 | 16.5
2009-05-29 | 6:27 | 40.5 | 26 | 27 | 43.5 | 14.5
2009-05-29 | 6:30 | 40.5 | 26.5 | 27.5 | 44.5 | 14
2009-05-29 | 6:33 | 40.5 | 26.5 | 27.5 | 44.5 | 14
2009-05-29 | 6:36 | 40.5 | 26.5 | 27.5 | 44.5 | 14
2009-05-29 | 6:39 | 40.5 | 27 | 28 | 44.5 | 13.5
2009-05-29 | 6:42 | 40.5 | 27 | 28 | 44.5 | 13.5
2009-05-29 | 6:45 | 41 | 27.5 | 28.5 | 44.5 | 13.5
2009-05-29 | 6:48 | 40.5 | 27.5 | 28.5 | 44.5 | 13
2009-05-29 | 6:51 | 40.5 | 27.5 | 29 | 44.5 | 13
2009-05-29 | 6:54 | 40.5 | 28 | 29 | 44.5 | 12.5
2009-05-29 | 6:57 | 40.5 | 28 | 29 | 44.5 | 12.5
2009-05-29 | 7:00 | 37 | 28 | 29 | 44.5 | 9
2009-05-29 | 7:03 | 36.5 | 27.5 | 28.5 | 39 | 9
2009-05-29 | 7:06 | 36 | 28 | 28 | 35.5 | 8
2009-05-29 | 7:09 | 35 | 28 | 27.5 | 33
2009-05-29 | 17:48
2009-05-29 | 17:51 | 23 | 20.5 | 21 | 21
2009-05-29 | 17:54 | 23 | 20.5 | 21 | 21 | 2.5
2009-05-29 | 17:57 | 23 | 20.5 | 21 | 21 | 2.5
2009-05-29 | 18:00 | 20 | 19.5 | 19 | 20 | 0.5
2009-05-29 | 18:03 | 26 | 19 | 19 | 27 | 7
2009-05-29 | 18:06 | 28 | 19 | 19 | 29 | 9
2009-05-29 | 18:09 | 29 | 20 | 20 | 30 | 9
2009-05-29 | 18:12 | 29.5 | 20.5 | 20.5 | 30.5 | 9
2009-05-29 | 18:15 | 30 | 21 | 21 | 31 | 9
2009-05-29 | 18:18 | 30 | 21 | 21 | 31.5 | 9
2009-05-29 | 18:21 | 30.5 | 21.5 | 21.5 | 31.5 | 9
2009-05-29 | 18:24 | 31 | 22 | 21.5 | 32 | 9
2009-05-29 | 18:27 | 31 | 22 | 22 | 32 | 9
2009-05-29 | 18:30 | 33 | 22.5 | 22.5 | 32 | 10.5
2009-05-29 | 18:33 | 32.5 | 23.5 | 22.5 | 31.5 | 9
2009-05-29 | 18:36 | 32 | 24 | 22.5 | 31 | 8
2009-05-29 | 18:39 | 32 | 24 | 22.5 | 31 | 8
2009-05-29 | 18:42 | 32 | 24 | 22.5 | 30.5 | 8
2009-05-29 | 18:45 | 31.5 | 24 | 22.5 | 30 | 7.5
2009-05-29 | 18:48 | 31.5 | 23.5 | 22.5 | 30 | 8
2009-05-29 | 18:51 | 31.5 | 23.5 | 22.5 | 29.5 | 8
2009-05-29 | 18:54 | 31.5 | 23 | 22.5 | 29 | 8.5
2009-05-29 | 18:57 | 31 | 23 | 22.5 | 29 | 8
2009-05-29 | 19:00 | 31 | 23 | 22.5 | 28.5 | 8
2009-05-29 | 19:03 | 30.5 | 22.5 | 22.5 | 28 | 8
2009-05-29 | 19:06 | 30.5 | 22.5 | 22.5 | 28 | 8
2009-05-29 | 19:09 | 30 | 22.5 | 22.5 | 27.5
|  | m³/hr | gal/ min | lit/sec | Kwatts | lit/sec. | tem diff
|  | 0.56 | 2.0496 | 0.1568 | 6 | 0.1568 | 9.1108 | 9
|  | m³/hr | gal/ min | lit/sec | Kwatts | lit/sec. | tem diff
|  | 0.24 | 0.8784 | 0.0672 | 6 | 0.0672 | 21.2585 | 21.5

## Parts
|  |  | Supplier | Part no | notes
Compressor | RK5480C | 1 | Wolseley
Condenser | Plate ApfaLaval CB52 16 or 12 plate | 1 | Stock
Evaporator | Plate ApfaLaval CB52 16 or 12 plate | 1 | Stock
Suction-liquid heat-exchanger | Fabricated from copper | 1
TEV | Parker SE-1/2-1.1/2VW R22/407C- 3/8", 1/2" | 1 | RCL | IPAR669
Accumulator? | May not be needed - already fitted to compressor | 1
Drier | 1/4" Drier C-052 | 1 | RCL | SPOR107
Sight glass | 1/4" SA12s | 1 | RCL | SPOR012
HP high pressure cutout | 061F7505 261 psi, 20 bar Button auto cutout | 2 | RCL | MSAG052
HP high pressure cutout | 061F7508 377 psi, 20 bar Button auto cutout | 1 | RCL | MSAG054
Low pressure cutout | 061F7525 25 psi, 1.72 bar Button auto cutout | 2 | RCL | MSAG007
Low pressure cutout | 061F7522 10 psi, 0.69 bar Button auto cutout | 1 | RCL | MSAG005
Pipework | 1/4" , 3/8" liquid and discharge, 3/8" suction.
copper fittings | 1/4" tees | 3 | RCL | KCFT570 | 1.47
| 3/8" tees | 4 | RCL | KCFT572 | 1.47
| 1/2" tees | 1 | RCL | KCFT573 | 1
| 5/8" tees | 2 | RCL | KCFT574 | 1.29
| 3/8" to 1/4" m-f reducer | 5 | RCL | KCFT195 | 0.5
| 5/8" to 1/2" m-f reducer | 4 | RCL | KCFT198
| 7/8" to 1/2" m-f reducer | 1 | RCL | KCFT205 | 0.8
charging ports | 1/4 charging port with 1/4" copper tail | 2 | RCL
Electrics
Compressor contactor | Moeller |  | RS
Compressor overload | Moeller 2.5 to 4A |  | RS
Digital thermostat | Eliwell IC902 |  | RCL
Transformer | 12v Eliwell |  | RCL
box and connectors | 220 x 200 x 140 |  | RS
Frost thermostat | Auto reset. (Calorex type) |  | Calorex
Discharge thermostat | Manual reset |  | stock
Indicator lights
Hours-run meter |  |  | stock
isolation switch
Source
fittings to evaporator
Source pump 15-50
3 x 100m 25mm dia
Glycol
Load side
Alpha2 15-15
exp vessel
Electrics
Sealed IP65 control box
Compressor contactor
Motor overload (3A)
Digital thermostat
(pressure switches listed above)
|  |  | inch | mm
Copper pipe od |  | 3/16 | 0.1875 | 4.7625
|  | 1/4 | 0.25 | 6.35
|  | 3/8 | 0.375 | 9.525
|  | 1/2 | 0.5 | 12.7
|  | 5/8 | 0.625 | 15.875
|  | 3/4 | 0.75 | 19.05
|  | 7/8 | 0.875 | 22.225
|  | 1 1/8 | 1.128 | 28.6512
|  | 1 3/8 | 1.375 | 34.925

## RK-HG compr
| RK 5480 | RK5490
Some approximate figures for Ian Taylor
| R407C | evap | cond | input | ref | heat out | COP
|  | °C | °C | watts | watts | watts
| RK5480 | 0 | 40 | 452 | 1704 | 2156 | 4.7699
| RK5490 | 0 | 40 | 513 | 1960 | 2473 | 4.8207
| RK5480 | 3 | 45 | 510 | 1671 | 2181 | 4.2765 | note, assume no sub-cool, so actual performance better
| RK5490 | 3 | 45 | 579 | 1804 | 2383 | 4.1157
let us assume that heat output is 2 to 2.5 kW with R290 propane
Assume evaporating at 0°C, and condensing at 40°C
| refrigeration duty |  | 1.7 | kW
|  |  | 5798.7 | BTU/hr
|  |  | 0.48322 | Tonnes
EXPANSION VALVE SIZE >> |  |  | This indicates that we need a nominal 1/2 tonne expansion valve, but the pressure across our valve is very low. No data available

## old parts list
|  |  | Supplier | Part no
Compressor | RK5480C | 1 | Wolseley |  | 230
Condenser | Plate ApfaLaval CB52 16 or 12 plate | 1 | Stock |  | 200
Evaporator | Plate ApfaLaval CB52 16 or 12 plate | 1 | Stock |  | 200
Suction-liquid heat-exchanger | Fabricated from copper | 1 |  |  | 79
TEV | Parker SE-1/2-1.1/2VW R22/407C- 3/8", 1/2" | 1 | RCL | IPAR669 | 54
Accumulator? | May not be needed - already fitted to compressor | 1 |  |  | 60
drier | 3/8" | 1 | RCL |  | 15
sight glass | 3/8" | 1 |  |  | 10
HP high pressure cutout |  |  |  |  | 848
Low pressure cutout
Pipework |  |  |  |  | 30
HP/LP |  |  |  |  | 28
copper fittings |  |  |  |  | 20
charging ports |  |  |  |  | 12
90
Electrics
Compressor contactor |  |  |  |  | 20
Digital thermostat |  |  |  |  | 80
box and connectors |  |  |  |  | 100
200
Source
fittings to evaporator |  |  |  |  | 30
Source pump 15-50 |  |  |  |  | 60
2 x 100m 25mm dia |  |  |  |  | 100
Glycol |  |  |  |  | 100
290
Load side
Alpha2 15-15 |  |  |  |  | 90
exp vessel |  |  |  |  | 25
115
Grand total, parts |  |  |  |  | 1543
time to piece together | 1 week at 150 = 750 |  |  |  | 750
GRAND TOTAL |  |  |  |  | 2293

## misc
from PH |  |  |  | blue figures are mm from graph
1 | 5k superheat |  | + 10k heat exchange | 20K heat exchange | 30K | lots!
| suct temp | 5 | 15 | 25 | 35 | 64!
| input | 19.5 | 20.5 | 21.5 | 22.5 | 24
| heat | 93 | 99 | 106 | 111 | 123
| COP | 4.7692 | 4.8293 | 4.9302 | 4.9333 | 5.125
|  | 0 | 1.259% | 3.376% | 3.441% | 7.46%
discharge | °C | 62 | 72 | 80 | 92 | 118
|  | 0 | 5 | 10 | 15 | 28
heat-exchange wattege |  | 0 | 101.0101 | 188.6792 | 270.2703 | 455.2846 | watts
Heatexchage
liquid in |  | 40 | 40 | 40 | 40 | 40
liquid out |  | 40 | 30 | 20 | 10 | 0
vapour in |  | 5 | 5 | 5 | 5 | 5
vapour out |  | 5 | 15 | 25 | 35 | 62
not possible!
dt |  | 0 | 10 | 20 | 30 | 40
dt |  | 0 | 10 | 20 | 30 | 57
1000 | watts | 1 | m²
100 |  | 0.1