## Conference Room
Terry Franklin |  |  | Host Connected (LGR S/N: 1248735) | Stopped (LGR S/N: 1248735) | End Of File (LGR S/N: 1248735)
2015-10-29
Engr 115
Plot Title: Conference room | [5 empty] | Input Parameters
# | Date Time, GMT-07:00 | CO2, ppm (LGR S/N: 1248735, SEN S/N: 1248735, LBL: Carbon Dioxide) | time (hr) | CO2 (ppm) after correction |  | assumption outside (ppm)= | 400
1 | 2015-10-22 14:55 | 708.2 | 0.016667 | 689.4 |  | recorded outside (ppm)= | 418.8
2 | 2015-10-22 14:56 | 536.6 | 0.033333 | 517.8 |  | conversion factor (ppm)= | -18.8
3 | 2015-10-22 14:57 | 456.7 | 0.05 | 437.9 |  | volume of room -m3 | 61.3
4 | 2015-10-22 14:58 | 442 | 0.066667 | 423.2 |  | Room Capacity | 10
5 | 2015-10-22 14:59 | 446.9 | 0.083333 | 428.1
6 | 2015-10-22 15:00 | 449.9 | 0.1 | 431.1
7 | 2015-10-22 15:01 | 586.1 | 0.11667 | 567.3 |  | volume of room- ft3 | 2164.7891
8 | 2015-10-22 15:02 | 509.8 | 0.13333 | 491
9 | 2015-10-22 15:03 | 432.8 | 0.15 | 414 |  | Calculations
10 | 2015-10-22 15:04 | 431 | 0.16667 | 412.2 |  | Air exchange rate- (1/hr) | 3.252
11 | 2015-10-22 15:05 | 523.2 | 0.18333 | 504.4 |  | Time to remove non-reactive chemical- hr | 0.92251
12 | 2015-10-22 15:06 | 812 | 0.2 | 793.2 |  | Ventilation Rate- scfm/person | 11.7332
13 | 2015-10-22 15:07 | 744.2 | 0.21667 | 725.4
14 | 2015-10-22 15:08 | 677 | 0.23333 | 658.2
15 | 2015-10-22 15:09 | 648.4 | 0.25 | 629.6
16 | 2015-10-22 15:10 | 659.3 | 0.26667 | 640.5
17 | 2015-10-22 15:11 | 670.9 | 0.28333 | 652.1 |  | lamda (min)= | 0.0542
18 | 2015-10-22 15:12 | 710 | 0.3 | 691.2 |  | lamda (hr)= | 3.252
19 | 2015-10-22 15:13 | 762.5 | 0.31667 | 743.7
20 | 2015-10-22 15:14 | 763.7 | 0.33333 | 744.9
21 | 2015-10-22 15:15 | 744.2 | 0.35 | 725.4
22 | 2015-10-22 15:16 | 725.3 | 0.36667 | 706.5
23 | 2015-10-22 15:17 | 731.4 | 0.38333 | 712.6
24 | 2015-10-22 15:18 | 738.1 | 0.4 | 719.3
25 | 2015-10-22 15:19 | 747.9 | 0.41667 | 729.1
26 | 2015-10-22 15:20 | 747.9 | 0.43333 | 729.1
27 | 2015-10-22 15:21 | 742.4 | 0.45 | 723.6
28 | 2015-10-22 15:22 | 747.3 | 0.46667 | 728.5
29 | 2015-10-22 15:23 | 749.1 | 0.48333 | 730.3
30 | 2015-10-22 15:24 | 750.9 | 0.5 | 732.1
31 | 2015-10-22 15:25 | 754 | 0.51667 | 735.2
32 | 2015-10-22 15:26 | 754 | 0.53333 | 735.2
33 | 2015-10-22 15:27 | 752.7 | 0.55 | 733.9
34 | 2015-10-22 15:28 | 763.7 | 0.56667 | 744.9
35 | 2015-10-22 15:29 | 774.7 | 0.58333 | 755.9
36 | 2015-10-22 15:30 | 794.9 | 0.6 | 776.1
37 | 2015-10-22 15:31 | 808.9 | 0.61667 | 790.1
38 | 2015-10-22 15:32 | 805.9 | 0.63333 | 787.1
39 | 2015-10-22 15:33 | 804 | 0.65 | 785.2
40 | 2015-10-22 15:34 | 805.9 | 0.66667 | 787.1
41 | 2015-10-22 15:35 | 799.1 | 0.68333 | 780.3
42 | 2015-10-22 15:36 | 797.3 | 0.7 | 778.5 | time (min | Lamda x t
43 | 2015-10-22 15:37 | 870.6 | 0.71667 | 851.8 | 0 | 0
44 | 2015-10-22 15:38 | 855.9 | 0.73333 | 837.1 | 1 | 0.033078
45 | 2015-10-22 15:39 | 819.9 | 0.75 | 801.1 | 2 | 0.11903
46 | 2015-10-22 15:40 | 809.5 | 0.76667 | 790.7 | 3 | 0.1453
47 | 2015-10-22 15:41 | 786.3 | 0.78333 | 767.5 | 4 | 0.20652
48 | 2015-10-22 15:42 | 741.1 | 0.8 | 722.3 | 5 | 0.33776
49 | 2015-10-22 15:43 | 722.8 | 0.81667 | 704 | 6 | 0.39621
50 | 2015-10-22 15:44 | 700.2 | 0.83333 | 681.4 | 7 | 0.47346
51 | 2015-10-22 15:45 | 675.2 | 0.85 | 656.4 | 8 | 0.5665
52 | 2015-10-22 15:46 | 669.1 | 0.86667 | 650.3 | 9 | 0.59058
53 | 2015-10-22 15:47 | 656.3 | 0.88333 | 637.5 | 10 | 0.64307
54 | 2015-10-22 15:48 | 649.6 | 0.9 | 630.8 | 11 | 0.67169
55 | 2015-10-22 15:49 | 640.4 | 0.91667 | 621.6 | 12 | 0.71237
56 | 2015-10-22 15:50 | 620.3 | 0.93333 | 601.5 | 13 | 0.80745
57 | 2015-10-22 15:51 | 606.2 | 0.95 | 587.4 | 14 | 0.87999
58 | 2015-10-22 15:52 | 594.6 | 0.96667 | 575.8 | 15 | 0.94389
59 | 2015-10-22 15:53 | 587.9 | 0.98333 | 569.1 | 16 | 0.98275
60 | 2015-10-22 15:54 | 578.1 | 1 | 559.3 | 17 | 1.0425
61 | 2015-10-22 15:55 | 576.3 | 1.0167 | 557.5 | 18 | 1.0538
62 | 2015-10-22 15:56 | 571.4 | 1.0333 | 552.6 | 19 | 1.0854
63 | 2015-10-22 15:57 | 564.1 | 1.05 | 545.3 | 20 | 1.1344
64 | 2015-10-22 15:58 | 555.6 | 1.0667 | 536.8 | 21 | 1.1947
65 | 2015-10-22 15:59 | 551.9 | 1.0833 | 533.1 | 22 | 1.2221
66 | 2015-10-22 16:00 | 545.8 | 1.1 | 527 | 23 | 1.2691
67 | 2015-10-22 16:01 | 534.2 | 1.1167 | 515.4 | 24 | 1.3648
68 | 2015-10-22 16:02 | 530.5 | 1.1333 | 511.7 | 25 | 1.3974
69 | 2015-10-22 16:03 | 523.2 | 1.15 | 504.4 | 26 | 1.465
70 | 2015-10-22 16:04 | 520.1 | 1.1667 | 501.3 | 27 | 1.4952
71 | 2015-10-22 16:05 | 517.7 | 1.1833 | 498.9 | 28 | 1.5191
72 | 2015-10-22 16:06 | 514.7 | 1.2 | 495.9 | 29 | 1.5499
73 | 2015-10-22 16:07 | 585.5 | 1.2167 | 566.7 | 30 | 0.99704
74 | 2015-10-22 16:08 | 630 | 1.2333 | 611.2
75 | 2015-10-22 16:09 | 631.9 | 1.25 | 613.1
76 | 2015-10-22 16:10 | 619.7 | 1.2667 | 600.9
77 | 2015-10-22 16:11 | 627 | 1.2833 | 608.2
78 | 2015-10-22 16:12 | 627.6 | 1.3 | 608.8
79 | 2015-10-22 16:13 | 625.2 | 1.3167 | 606.4
80 | 2015-10-22 16:14 | 631.9 | 1.3333 | 613.1
81 | 2015-10-22 16:15 | 554.3 | 1.35 | 535.5
82 | 2015-10-22 16:16 | 420.6 | 1.3667 | 401.8
83 | 2015-10-22 16:17 | 413.9 | 1.3833 | 395.1
84 | 2015-10-22 16:18 | 424.9 | 1.4 | 406.1
85 | 2015-10-22 16:19 | 418.8 | 1.4167 | 400
86 | 2015-10-22 16:20 | 426.7 | 1.4333 | 407.9
87 | 2015-10-22 16:21 | 435.3 | 1.45 | 416.5
88 | 2015-10-22 16:22 | 550.7 | 1.4667 | 531.9
89 | 2015-10-22 16:23 | 801 | 1.4833 | 782.2
90 | 2015-10-22 16:24 | 717.9 | 1.5 | 699.1
91 | 2015-10-22 16:25 | 627.6 | 1.5167 | 608.8
92 | 2015-10-22 16:26
93 | 2015-10-22 16:26 |  | Logged
|  |  |  | Logged | Logged

## Questions
1 | 3.252 air exhchanges per hour
2 | The time it takes to remove non reactive material is about 0.93 hours. I would recommend them to open windows if they were working with non-reactive chemicals.
3 | The ventilation rate is 11.7 scfm/person. This is less than the ASHRAC ventilation rate of 15 scfm/person. These are relatively close rates but our room's rate is less. This means that the occupants should create more ventialtion and supply more air into the room.
4 | If the occupancy was 7 people, the rate would be a little more than 15scfm/person. 7 people is what the occupancy of the room should be.