## Raw Data
Plot Title: LibraryStudyRoom
# | Date Time, GMT-07:00 | CO2, ppm
1 | 2013-09-20 11:45 | 631.9
2 | 2013-09-20 11:46 | 629.4
3 | 2013-09-20 11:47 | 461.5
4 | 2013-09-20 11:48 | 446.3
5 | 2013-09-20 11:49 | 437.7
6 | 2013-09-20 11:50 | 437.7
7 | 2013-09-20 11:51 | 451.2
8 | 2013-09-20 11:52 | 817.5
9 | 2013-09-20 11:53 | 678.3
10 | 2013-09-20 11:54 | 541.5
11 | 2013-09-20 11:55 | 618.4
12 | 2013-09-20 11:56 | 503.1
13 | 2013-09-20 11:57 | 498.8
14 | 2013-09-20 11:58 | 498.8
15 | 2013-09-20 11:59 | 540.9
16 | 2013-09-20 12:00 | 538.5
17 | 2013-09-20 12:01 | 583.6
18 | 2013-09-20 12:02 | 522.6
19 | 2013-09-20 12:03 | 506.7
20 | 2013-09-20 12:04 | 1221.6
21 | 2013-09-20 12:05 | 605
22 | 2013-09-20 12:06 | 607.4
23 | 2013-09-20 12:07 | 583
24 | 2013-09-20 12:08 | 578.1
25 | 2013-09-20 12:09 | 576.9
26 | 2013-09-20 12:10 | 569.6
27 | 2013-09-20 12:11 | 574.5
28 | 2013-09-20 12:12 | 586.7
29 | 2013-09-20 12:13 | 591.6
30 | 2013-09-20 12:14 | 590.4
31 | 2013-09-20 12:15 | 587.3
32 | 2013-09-20 12:16 | 576.3
33 | 2013-09-20 12:17 | 572.6
34 | 2013-09-20 12:18 | 571.4
35 | 2013-09-20 12:19 | 573.3
36 | 2013-09-20 12:20 | 567.8
37 | 2013-09-20 12:21 | 560.4
38 | 2013-09-20 12:22 | 557.4
39 | 2013-09-20 12:23 | 555.6
40 | 2013-09-20 12:24 | 556.8
41 | 2013-09-20 12:25 | 550.7
42 | 2013-09-20 12:26 | 548.8
43 | 2013-09-20 12:27 | 549.5
44 | 2013-09-20 12:28 | 548.8
45 | 2013-09-20 12:29 | 549.5
46 | 2013-09-20 12:30 | 547.6
47 | 2013-09-20 12:31 | 546.4
48 | 2013-09-20 12:32 | 548.2
49 | 2013-09-20 12:33 | 552.5
50 | 2013-09-20 12:34 | 573.9
51 | 2013-09-20 12:35 | 581.2
52 | 2013-09-20 12:36 | 575.7
53 | 2013-09-20 12:37 | 564.1
54 | 2013-09-20 12:38 | 556.8
55 | 2013-09-20 12:39 | 769.2
56 | 2013-09-20 12:40 | 667.3
57 | 2013-09-20 12:41 | 630
58 | 2013-09-20 12:42 | 605
59 | 2013-09-20 12:43 | 603.2
60 | 2013-09-20 12:44 | 589.7
61 | 2013-09-20 12:45 | 582.4
62 | 2013-09-20 12:46 | 575.7
63 | 2013-09-20 12:47 | 564.7
64 | 2013-09-20 12:48 | 557.4
65 | 2013-09-20 12:49 | 549.5
66 | 2013-09-20 12:50 | 551.9
67 | 2013-09-20 12:51 | 551.9
68 | 2013-09-20 12:52 | 552.5
69 | 2013-09-20 12:53 | 549.5
70 | 2013-09-20 12:54 | 547.6
71 | 2013-09-20 12:55 | 547
72 | 2013-09-20 12:56 | 530.5
73 | 2013-09-20 12:57 | 525.6
74 | 2013-09-20 12:58 | 518.9
75 | 2013-09-20 12:59 | 514
76 | 2013-09-20 13:00 | 506.7
77 | 2013-09-20 13:01 | 498.8
78 | 2013-09-20 13:02 | 489.6
79 | 2013-09-20 13:03 | 484.7
80 | 2013-09-20 13:04 | 487.2
81 | 2013-09-20 13:05 | 583.6
82 | 2013-09-20 13:06 | 578.8
83 | 2013-09-20 13:07 | 572.6
84 | 2013-09-20 13:08 | 548.8
85 | 2013-09-20 13:09 | 515.9
86 | 2013-09-20 13:10 | 503.1
87 | 2013-09-20 13:11 | 493.3
88 | 2013-09-20 13:12 | 492.7
89 | 2013-09-20 13:13 | 485.3
90 | 2013-09-20 13:14 | 478.6
91 | 2013-09-20 13:15 | 476.2
92 | 2013-09-20 13:16 | 474.4
93 | 2013-09-20 13:17 | 478
94 | 2013-09-20 13:18 | 481.1
95 | 2013-09-20 13:19 | 479.2
96 | 2013-09-20 13:20 | 475.6
97 | 2013-09-20 13:21 | 476.2
98 | 2013-09-20 13:22 | 476.2
99 | 2013-09-20 13:23 | 476.2
100 | 2013-09-20 13:24 | 485.3
101 | 2013-09-20 13:25 | 519.5
102 | 2013-09-20 13:26 | 528.7
103 | 2013-09-20 13:27 | 517.1
104 | 2013-09-20 13:28 | 514.7
105 | 2013-09-20 13:29 | 504.9

## Air Exchange Rate Analysis
Allison Tapaya
ENG 115
2013-09-20
Input Parameters:
Measured C-outside [ppm] | 420
Assumed C-outside [ppm] | 400
Correction Factor [ppm] | 20
Volume [ft3] | 2323.732
Room Capacity [people] | 8
Calculations:
Air Exchange Rate [per hour] | 3.2832
Time to remove nonreacctive chemical [hour] | 0.91374
Ventilation Rate [ft3/min per person] | 15.8943
Analysis
Measure | Date and Time | Hobo CO2 concentration | CO2 concentration [ppm] | Experiment time [hours] | -ln((Croom-Coutside)/(Co-Coutside))
0 | 2013-09-20 12:40 | 667.3 | 647.3 | 0 | 0
1 | 2013-09-20 12:41 | 630 | 610 | 0.016667 | 0.16349
2 | 2013-09-20 12:42 | 605 | 585 | 0.033333 | 0.29025
3 | 2013-09-20 12:43 | 603.2 | 583.2 | 0.05 | 0.30002
4 | 2013-09-20 12:44 | 589.7 | 569.7 | 0.066667 | 0.37657
5 | 2013-09-20 12:45 | 582.4 | 562.4 | 0.083333 | 0.42054
6 | 2013-09-20 12:46 | 575.7 | 555.7 | 0.1 | 0.46267
7 | 2013-09-20 12:47 | 564.7 | 544.7 | 0.11667 | 0.53594
8 | 2013-09-20 12:48 | 557.4 | 537.4 | 0.13333 | 0.58771
9 | 2013-09-20 12:49 | 549.5 | 529.5 | 0.15 | 0.64692
10 | 2013-09-20 12:50 | 551.9 | 531.9 | 0.16667 | 0.62856
11 | 2013-09-20 12:51 | 551.9 | 531.9 | 0.18333 | 0.62856
12 | 2013-09-20 12:52 | 552.5 | 532.5 | 0.2 | 0.62402
13 | 2013-09-20 12:53 | 549.5 | 529.5 | 0.21667 | 0.64692
14 | 2013-09-20 12:54 | 547.6 | 527.6 | 0.23333 | 0.6617
15 | 2013-09-20 12:55 | 547 | 527 | 0.25 | 0.66642
16 | 2013-09-20 12:56 | 530.5 | 510.5 | 0.26667 | 0.80559
17 | 2013-09-20 12:57 | 525.6 | 505.6 | 0.28333 | 0.85094
18 | 2013-09-20 12:58 | 518.9 | 498.9 | 0.3 | 0.91649
19 | 2013-09-20 12:59 | 514 | 494 | 0.31667 | 0.96731
20 | 2013-09-20 13:00 | 506.7 | 486.7 | 0.33333 | 1.0481
21 | 2013-09-20 13:01 | 498.8 | 478.8 | 0.35 | 1.1437
22 | 2013-09-20 13:02 | 489.6 | 469.6 | 0.36667 | 1.2678
23 | 2013-09-20 13:03 | 484.7 | 464.7 | 0.38333 | 1.3408

## Concentration Analysis
Allison Tapaya
ENG 115
2013-09-20
Input Parameters:
Measured C-outside [ppm] | 420
Assumed C-outside [ppm] | 400
Correction Factor [ppm] | 20
Analysis
Measure | Date and Time | Hobo CO2 concentration | CO2 concentration [ppm]
1 | 2013-09-20 11:45 | 631.9 | 611.9
2 | 2013-09-20 11:46 | 629.4 | 609.4
3 | 2013-09-20 11:47 | 461.5 | 441.5
4 | 2013-09-20 11:48 | 446.3 | 426.3
5 | 2013-09-20 11:49 | 437.7 | 417.7
6 | 2013-09-20 11:50 | 437.7 | 417.7
7 | 2013-09-20 11:51 | 451.2 | 431.2
8 | 2013-09-20 11:52 | 817.5 | 797.5
9 | 2013-09-20 11:53 | 678.3 | 658.3
10 | 2013-09-20 11:54 | 541.5 | 521.5
11 | 2013-09-20 11:55 | 618.4 | 598.4
12 | 2013-09-20 11:56 | 503.1 | 483.1
13 | 2013-09-20 11:57 | 498.8 | 478.8
14 | 2013-09-20 11:58 | 498.8 | 478.8
15 | 2013-09-20 11:59 | 540.9 | 520.9
16 | 2013-09-20 12:00 | 538.5 | 518.5
17 | 2013-09-20 12:01 | 583.6 | 563.6
18 | 2013-09-20 12:02 | 522.6 | 502.6
19 | 2013-09-20 12:03 | 506.7 | 486.7
20 | 2013-09-20 12:04 | 1221.6 | 1201.6
21 | 2013-09-20 12:05 | 605 | 585
22 | 2013-09-20 12:06 | 607.4 | 587.4
23 | 2013-09-20 12:07 | 583 | 563
24 | 2013-09-20 12:08 | 578.1 | 558.1
25 | 2013-09-20 12:09 | 576.9 | 556.9
26 | 2013-09-20 12:10 | 569.6 | 549.6
27 | 2013-09-20 12:11 | 574.5 | 554.5
28 | 2013-09-20 12:12 | 586.7 | 566.7
29 | 2013-09-20 12:13 | 591.6 | 571.6
30 | 2013-09-20 12:14 | 590.4 | 570.4
31 | 2013-09-20 12:15 | 587.3 | 567.3
32 | 2013-09-20 12:16 | 576.3 | 556.3
33 | 2013-09-20 12:17 | 572.6 | 552.6
34 | 2013-09-20 12:18 | 571.4 | 551.4
35 | 2013-09-20 12:19 | 573.3 | 553.3
36 | 2013-09-20 12:20 | 567.8 | 547.8
37 | 2013-09-20 12:21 | 560.4 | 540.4
38 | 2013-09-20 12:22 | 557.4 | 537.4
39 | 2013-09-20 12:23 | 555.6 | 535.6
40 | 2013-09-20 12:24 | 556.8 | 536.8
41 | 2013-09-20 12:25 | 550.7 | 530.7
42 | 2013-09-20 12:26 | 548.8 | 528.8
43 | 2013-09-20 12:27 | 549.5 | 529.5
44 | 2013-09-20 12:28 | 548.8 | 528.8
45 | 2013-09-20 12:29 | 549.5 | 529.5
46 | 2013-09-20 12:30 | 547.6 | 527.6
47 | 2013-09-20 12:31 | 546.4 | 526.4
48 | 2013-09-20 12:32 | 548.2 | 528.2
49 | 2013-09-20 12:33 | 552.5 | 532.5
50 | 2013-09-20 12:34 | 573.9 | 553.9
51 | 2013-09-20 12:35 | 581.2 | 561.2
52 | 2013-09-20 12:36 | 575.7 | 555.7
53 | 2013-09-20 12:37 | 564.1 | 544.1
54 | 2013-09-20 12:38 | 556.8 | 536.8
55 | 2013-09-20 12:39 | 769.2 | 749.2
56 | 2013-09-20 12:40 | 667.3 | 647.3
57 | 2013-09-20 12:41 | 630 | 610
58 | 2013-09-20 12:42 | 605 | 585
59 | 2013-09-20 12:43 | 603.2 | 583.2
60 | 2013-09-20 12:44 | 589.7 | 569.7
61 | 2013-09-20 12:45 | 582.4 | 562.4
62 | 2013-09-20 12:46 | 575.7 | 555.7
63 | 2013-09-20 12:47 | 564.7 | 544.7
64 | 2013-09-20 12:48 | 557.4 | 537.4
65 | 2013-09-20 12:49 | 549.5 | 529.5
66 | 2013-09-20 12:50 | 551.9 | 531.9
67 | 2013-09-20 12:51 | 551.9 | 531.9
68 | 2013-09-20 12:52 | 552.5 | 532.5
69 | 2013-09-20 12:53 | 549.5 | 529.5
70 | 2013-09-20 12:54 | 547.6 | 527.6
71 | 2013-09-20 12:55 | 547 | 527
72 | 2013-09-20 12:56 | 530.5 | 510.5
73 | 2013-09-20 12:57 | 525.6 | 505.6
74 | 2013-09-20 12:58 | 518.9 | 498.9
75 | 2013-09-20 12:59 | 514 | 494
76 | 2013-09-20 13:00 | 506.7 | 486.7
77 | 2013-09-20 13:01 | 498.8 | 478.8
78 | 2013-09-20 13:02 | 489.6 | 469.6
79 | 2013-09-20 13:03 | 484.7 | 464.7
80 | 2013-09-20 13:04 | 487.2 | 467.2
81 | 2013-09-20 13:05 | 583.6 | 563.6
82 | 2013-09-20 13:06 | 578.8 | 558.8
83 | 2013-09-20 13:07 | 572.6 | 552.6
84 | 2013-09-20 13:08 | 548.8 | 528.8
85 | 2013-09-20 13:09 | 515.9 | 495.9
86 | 2013-09-20 13:10 | 503.1 | 483.1
87 | 2013-09-20 13:11 | 493.3 | 473.3
88 | 2013-09-20 13:12 | 492.7 | 472.7
89 | 2013-09-20 13:13 | 485.3 | 465.3
90 | 2013-09-20 13:14 | 478.6 | 458.6
91 | 2013-09-20 13:15 | 476.2 | 456.2
92 | 2013-09-20 13:16 | 474.4 | 454.4
93 | 2013-09-20 13:17 | 478 | 458
94 | 2013-09-20 13:18 | 481.1 | 461.1
95 | 2013-09-20 13:19 | 479.2 | 459.2
96 | 2013-09-20 13:20 | 475.6 | 455.6
97 | 2013-09-20 13:21 | 476.2 | 456.2
98 | 2013-09-20 13:22 | 476.2 | 456.2
99 | 2013-09-20 13:23 | 476.2 | 456.2
100 | 2013-09-20 13:24 | 485.3 | 465.3
101 | 2013-09-20 13:25 | 519.5 | 499.5
102 | 2013-09-20 13:26 | 528.7 | 508.7
103 | 2013-09-20 13:27 | 517.1 | 497.1
104 | 2013-09-20 13:28 | 514.7 | 494.7
105 | 2013-09-20 13:29 | 504.9 | 484.9

## Answers to Questions
Answers to Questions
1. What is the air exchange rate (λ) of the room you tested? Be sure to include the units for the air exchange rate in your answer.
The air exchange rate in the library study room we tested was 3.2832 per hour.
2. What does your air exchange rate tell you about the potential for indoor air problems in the room you tested? In general it takes 3/λ hours to remove a non-reactive chemical from indoor air. Based on this time, what recommendations would you make to the occupants of the room?
For our library test room exchange rate of 3.2832 per hour it would take 0.914 hours to remove non-reactive chemicals from the room. For our testing the air conditioning was turned on during the whole time of the expirement with no other ways for air to be exchanged in the room. However, if the air conditioning was not on it would take much longer for the air to exchange, therefore I recommend that if there are the maximum capacity of people in this room the door be left open and the air conditioning be kept on. However, one to three people in this room with the door shut and air conditiong on should be safe.
3. Compare your ventilation rate for a typical number of occupants to the ASHRAE recommended ventilation rate. Based on this comparison are the occupants wasting energy heating and cooling the air or are the occupants being too cheap and not supplying enough air? Justify your answer.
The ASHRAE recommended ventilation rate is 15 scfm/ person. Our ventilation rate for the library study room was 15.894 scfm/ person. Although this rate is not to much greater than what ASHRAE recomments for reasonable levels of CO2 it is still rather high for a room this size. I do not think the occupants are being too cheap or aren't supplying enough air because the air conditioning seemed to be the biggest help of all for better ventilation in the room, the room was just poorly designed. By simply leaving the door open with the air conditioning running would probably help allow CO2 to flow out of the room at a faster rate.
4. Given the ASHRAE standard ventilation standard, what is the maximum number of people would you recommend having in this room at one time?
The ventialtion rate from our experiment was calculated with four occupants, however the room has enough seats for eight or more. I do not recommend there being more than five people in the room if the door is closed, even with four people it was pushing ASHREA ventilation rate standard.However, if the door to the room was left wide open it may be safe to have up to 7 people in the room with the air conditioning on as well.