## Concentration Analysis
Shannon McHatton
ENGR 115
Lab 2-5
Sept. 21, 2012
Input Parameters
Measured Coutside [ppm] | 402
Assumed Coutside [ppm] | 400
Correction Factor [ppm] | -2
Analysis
Measurement | Date and Time | Hobo CO2 Concentration | Experiment Time [hr] | CO2 Concentration [ppm]
1 | 2012-09-14 14:45 | 677 | 0.016667 | 675
2 | 2012-09-14 14:46 | 492.7 | 0.033333 | 490.7
3 | 2012-09-14 14:47 | 470.7 | 0.05 | 468.7
4 | 2012-09-14 14:48 | 420.6 | 0.066667 | 418.6
5 | 2012-09-14 14:49 | 401.1 | 0.083333 | 399.1
6 | 2012-09-14 14:50 | 417.6 | 0.1 | 415.6
7 | 2012-09-14 14:51 | 418.8 | 0.11667 | 416.8
8 | 2012-09-14 14:52 | 418.8 | 0.13333 | 416.8
9 | 2012-09-14 14:53 | 421.9 | 0.15 | 419.9
10 | 2012-09-14 14:54 | 410.9 | 0.16667 | 408.9
11 | 2012-09-14 14:55 | 409 | 0.18333 | 407
12 | 2012-09-14 14:56 | 407.2 | 0.2 | 405.2
13 | 2012-09-14 14:57 | 489.6 | 0.21667 | 487.6
14 | 2012-09-14 14:58 | 458.5 | 0.23333 | 456.5
15 | 2012-09-14 14:59 | 720.4 | 0.25 | 718.4
16 | 2012-09-14 15:00 | 409 | 0.26667 | 407
17 | 2012-09-14 15:01 | 402.3 | 0.28333 | 400.3
18 | 2012-09-14 15:02 | 412.1 | 0.3 | 410.1
19 | 2012-09-14 15:03 | 412.1 | 0.31667 | 410.1
20 | 2012-09-14 15:04 | 402.9 | 0.33333 | 400.9
21 | 2012-09-14 15:05 | 402.3 | 0.35 | 400.3
22 | 2012-09-14 15:06 | 447.5 | 0.36667 | 445.5
23 | 2012-09-14 15:07 | 501.8 | 0.38333 | 499.8
24 | 2012-09-14 15:08 | 463.4 | 0.4 | 461.4
25 | 2012-09-14 15:09 | 445.1 | 0.41667 | 443.1
26 | 2012-09-14 15:10 | 431 | 0.43333 | 429
27 | 2012-09-14 15:11 | 421.2 | 0.45 | 419.2
28 | 2012-09-14 15:12 | 413.9 | 0.46667 | 411.9
29 | 2012-09-14 15:13 | 435.9 | 0.48333 | 433.9
30 | 2012-09-14 15:14 | 576.3 | 0.5 | 574.3
31 | 2012-09-14 15:15 | 601.3 | 0.51667 | 599.3
32 | 2012-09-14 15:16 | 596.5 | 0.53333 | 594.5
33 | 2012-09-14 15:17 | 607.4 | 0.55 | 605.4
34 | 2012-09-14 15:18 | 627 | 0.56667 | 625
35 | 2012-09-14 15:19 | 638 | 0.58333 | 636
36 | 2012-09-14 15:20 | 662.4 | 0.6 | 660.4
37 | 2012-09-14 15:21 | 720.4 | 0.61667 | 718.4
38 | 2012-09-14 15:22 | 745.4 | 0.63333 | 743.4
39 | 2012-09-14 15:23 | 838.2 | 0.65 | 836.2
40 | 2012-09-14 15:24 | 886.4 | 0.66667 | 884.4
41 | 2012-09-14 15:25 | 869.4 | 0.68333 | 867.4
42 | 2012-09-14 15:26 | 854.7 | 0.7 | 852.7
43 | 2012-09-14 15:27 | 854.7 | 0.71667 | 852.7
44 | 2012-09-14 15:28 | 866.3 | 0.73333 | 864.3
45 | 2012-09-14 15:29 | 909 | 0.75 | 907
46 | 2012-09-14 15:30 | 894.4 | 0.76667 | 892.4
47 | 2012-09-14 15:31 | 881 | 0.78333 | 879
48 | 2012-09-14 15:32 | 984.1 | 0.8 | 982.1
49 | 2012-09-14 15:33 | 962.1 | 0.81667 | 960.1
50 | 2012-09-14 15:34 | 956 | 0.83333 | 954
51 | 2012-09-14 15:35 | 979.2 | 0.85 | 977.2
52 | 2012-09-14 15:36 | 1001.2 | 0.86667 | 999.2
53 | 2012-09-14 15:37 | 974.4 | 0.88333 | 972.4
54 | 2012-09-14 15:38 | 1343.7 | 0.9 | 1341.7
55 | 2012-09-14 15:39 | 1166.1 | 0.91667 | 1164.1
56 | 2012-09-14 15:40 | 1148.4 | 0.93333 | 1146.4
57 | 2012-09-14 15:41 | 1142.2 | 0.95 | 1140.2
58 | 2012-09-14 15:42 | 1184.4 | 0.96667 | 1182.4
59 | 2012-09-14 15:43 | 1186.2 | 0.98333 | 1184.2
60 | 2012-09-14 15:44 | 1192.9 | 1 | 1190.9
61 | 2012-09-14 15:45 | 1203.9 | 1.0167 | 1201.9
62 | 2012-09-14 15:46 | 1212.5 | 1.0333 | 1210.5
63 | 2012-09-14 15:47 | 1214.3 | 1.05 | 1212.3
64 | 2012-09-14 15:48 | 1217.3 | 1.0667 | 1215.3
65 | 2012-09-14 15:49 | 1189.3 | 1.0833 | 1187.3
66 | 2012-09-14 15:50 | 1152 | 1.1 | 1150
67 | 2012-09-14 15:51 | 1113.6 | 1.1167 | 1111.6
68 | 2012-09-14 15:52 | 1087.3 | 1.1333 | 1085.3
69 | 2012-09-14 15:53 | 1078.8 | 1.15 | 1076.8
70 | 2012-09-14 15:54 | 1069 | 1.1667 | 1067
71 | 2012-09-14 15:55 | 1029.9 | 1.1833 | 1027.9
72 | 2012-09-14 15:56 | 1020.1 | 1.2 | 1018.1
73 | 2012-09-14 15:57 | 1018.3 | 1.2167 | 1016.3
74 | 2012-09-14 15:58 | 1019.5 | 1.2333 | 1017.5
75 | 2012-09-14 15:59 | 979.2 | 1.25 | 977.2
76 | 2012-09-14 16:00 | 973.1 | 1.2667 | 971.1
77 | 2012-09-14 16:01 | 957.9 | 1.2833 | 955.9
78 | 2012-09-14 16:02 | 947.5 | 1.3 | 945.5
79 | 2012-09-14 16:03 | 942.6 | 1.3167 | 940.6
80 | 2012-09-14 16:04 | 927.4 | 1.3333 | 925.4
81 | 2012-09-14 16:05 | 922.5 | 1.35 | 920.5
82 | 2012-09-14 16:06 | 902.9 | 1.3667 | 900.9
83 | 2012-09-14 16:07 | 893.2 | 1.3833 | 891.2
84 | 2012-09-14 16:08 | 588.5 | 1.4 | 586.5
85 | 2012-09-14 16:09 | 451.2 | 1.4167 | 449.2
86 | 2012-09-14 16:10 | 469.5 | 1.4333 | 467.5
87 | 2012-09-14 16:11 | 430.4 | 1.45 | 428.4
88 | 2012-09-14 16:12 | 438.9 | 1.4667 | 436.9
89 | 2012-09-14 16:13 | 424.3 | 1.4833 | 422.3
90 | 2012-09-14 16:14 | 420 | 1.5 | 418
91 | 2012-09-14 16:15 | 407.2 | 1.5167 | 405.2
92 | 2012-09-14 16:16 | 413.3 | 1.5333 | 411.3
93 | 2012-09-14 16:17 | 407.2 | 1.55 | 405.2
94 | 2012-09-14 16:18 | 591.6 | 1.5667 | 589.6
95 | 2012-09-14 16:19 | 629.4 | 1.5833 | 627.4
96 | 2012-09-14 16:19 |  | 1.6 | -2
97 | 2012-09-14 16:20 | 636.8 | 1.6167 | 634.8
98 | 2012-09-14 16:20 |  |  | Logged | Logged

## Air Exchange Rate Analysis
Shannon McHatton
ENGR 115
Lab 2-5
Sept. 21, 2012
Input Parameters
Measured Coutside [ppm] | 402
Assumed Coutside [ppm] | 400
Correction Factor [ppm] | -2
Volume of Room [cubic feet] | 1517.425
Room Capacity [people] | 4
Calculations
Air Exchange Rate [per hour] | 1.7368
Time to remove non-reactive chemical [hr] | 1.7273
Ventilation Rate [standard cubic feet per minute per person] | 10.9811
Analysis
Decay Measurement | Date and Time | Hobo CO2 Concentration | Decay Experiment Time [hr] | CO2 Concentration [ppm] | -ln((Cout(t)-Cin)/(Ct=0-Cin))
0 | 2012-09-14 15:48 | 1217.3 | 0 | 1215.3 | 0
1 | 2012-09-14 15:49 | 1189.3 | 0.016667 | 1187.3 | 0.034947
2 | 2012-09-14 15:50 | 1152 | 0.033333 | 1150 | 0.083483
3 | 2012-09-14 15:51 | 1113.6 | 0.05 | 1111.6 | 0.13604
4 | 2012-09-14 15:52 | 1087.3 | 0.066667 | 1085.3 | 0.1737
5 | 2012-09-14 15:53 | 1078.8 | 0.083333 | 1076.8 | 0.18618
6 | 2012-09-14 15:54 | 1069 | 0.1 | 1067 | 0.20077
7 | 2012-09-14 15:55 | 1029.9 | 0.11667 | 1027.9 | 0.26118
8 | 2012-09-14 15:56 | 1020.1 | 0.13333 | 1018.1 | 0.27691
9 | 2012-09-14 15:57 | 1018.3 | 0.15 | 1016.3 | 0.27982
10 | 2012-09-14 15:58 | 1019.5 | 0.16667 | 1017.5 | 0.27788
11 | 2012-09-14 15:59 | 979.2 | 0.18333 | 977.2 | 0.34537
12 | 2012-09-14 16:00 | 973.1 | 0.2 | 971.1 | 0.35599
13 | 2012-09-14 16:01 | 957.9 | 0.21667 | 955.9 | 0.38297
14 | 2012-09-14 16:02 | 947.5 | 0.23333 | 945.5 | 0.40185
15 | 2012-09-14 16:03 | 942.6 | 0.25 | 940.6 | 0.41088
16 | 2012-09-14 16:04 | 927.4 | 0.26667 | 925.4 | 0.4394
17 | 2012-09-14 16:05 | 922.5 | 0.28333 | 920.5 | 0.44877
18 | 2012-09-14 16:06 | 902.9 | 0.3 | 900.9 | 0.48715

## CO2 Lab Questions
Lab Questions
1. We tested a kitchen in Cypress dorms and found the air exchange rate to be 1.7368 per hr
2. The air exchange rate tells us that the room has good air circulation with approximately 5 people sitting in there. Potential problems will emerge when more people enter the room and maybe a few start cooking (stove, oven, microwave), in which case it would be in everbody's best interest to open a window, or some people leave the room. Using the equation 3/λ we find tht it takes about 1.73 hours to remove a non-reactive chemical from the indoor air. To keep things safe I would suggest no more than 5 people in the kitchen at a time unless there is significant air circulation.
3. The calculated ventilation rate for the cypress kitchen was 8.78 scf fo 5 occupants compared to the ASHRAE standard ventilation rate of 15 scf. If this is the amount it should be than I suppose the occupants are being to cheap and not supplying enough air. It is almost half of the standard ASHRAE and it is a kitchen which should have more air supply because of the many peoplewho share it, going in and out, and the appliances inside.
4. Given the ASHRAE standard ventilation standard is 15 scf, the maximum number of occupants in the cypress kitchen should be 4.