## CO2 Data
Sophia Pasinski |  |  |  | Air Exchange Rate | Ventilaton Rate Data
ENGR 115 |  |  |  | y= 0.0258x-0.0272 | λ (1/hour) | 1.548
November, 1 2019 |  |  |  | λ=0.0258 per minute | V (ft^3) (room volume) | 2221.2946
|  | Measured Coutdoor [ppm] | 456 |  | Room Capacity (people) | 4
|  | Assumed Coutdoor [ppm] | 400 |  | Ventilation Rate (scfm/person) | 14.3274
|  | Correction Factor [ppm] | -56
|  | Room Volume [m3] | 62.9
|  | Room Capacity (people) | 4
Plot Title: Library Study Room 2
# | Date Time, GMT-08:00 | Hobo CO2 concentratoin (ppm) | Actual CO2 Concentration (ppm) | λt
1 | 2014-02-14 14:44 | 756.4 | 700.4
2 | 2014-02-14 14:45 | 700.9 | 644.9
3 | 2014-02-14 14:46 | 610.5 | 554.5
4 | 2014-02-14 14:47 | 514 | 458
5 | 2014-02-14 14:48 | 495.7 | 439.7
6 | 2014-02-14 14:49 | 482.3 | 426.3
7 | 2014-02-14 14:50 | 471.9 | 415.9
8 | 2014-02-14 14:51 | 468.3 | 412.3
9 | 2014-02-14 14:52 | 464 | 408
10 | 2014-02-14 14:53 | 457.9 | 401.9
11 | 2014-02-14 14:54 | 456 | 400
12 | 2014-02-14 14:55 | 454.2 | 398.2
13 | 2014-02-14 14:56 | 457.9 | 401.9
14 | 2014-02-14 14:57 | 542.7 | 486.7
15 | 2014-02-14 14:58 | 547.6 | 491.6
16 | 2014-02-14 14:59 | 627.6 | 571.6
17 | 2014-02-14 15:00 | 655.7 | 599.7
18 | 2014-02-14 15:01 | 634.3 | 578.3
19 | 2014-02-14 15:02 | 622.7 | 566.7
20 | 2014-02-14 15:03 | 625.8 | 569.8
21 | 2014-02-14 15:04 | 663.6 | 607.6
22 | 2014-02-14 15:05 | 685.6 | 629.6
23 | 2014-02-14 15:06 | 705.7 | 649.7
24 | 2014-02-14 15:07 | 717.9 | 661.9
25 | 2014-02-14 15:08 | 733.8 | 677.8
26 | 2014-02-14 15:09 | 746 | 690
27 | 2014-02-14 15:10 | 765 | 709
28 | 2014-02-14 15:11 | 784.5 | 728.5
29 | 2014-02-14 15:12 | 796.7 | 740.7
30 | 2014-02-14 15:13 | 810.1 | 754.1
31 | 2014-02-14 15:14 | 823 | 767
32 | 2014-02-14 15:15 | 834.6 | 778.6
33 | 2014-02-14 15:16 | 849.8 | 793.8
34 | 2014-02-14 15:17 | 861.4 | 805.4
35 | 2014-02-14 15:18 | 871.2 | 815.2
36 | 2014-02-14 15:19 | 884 | 828
37 | 2014-02-14 15:20 | 891.3 | 835.3
38 | 2014-02-14 15:21 | 900.5 | 844.5
39 | 2014-02-14 15:22 | 909 | 853
40 | 2014-02-14 15:23 | 917 | 861
41 | 2014-02-14 15:24 | 921.9 | 865.9
42 | 2014-02-14 15:25 | 928 | 872
43 | 2014-02-14 15:26 | 937.1 | 881.1
44 | 2014-02-14 15:27 | 942.6 | 886.6
45 | 2014-02-14 15:28 | 945.7 | 889.7
46 | 2014-02-14 15:29 | 955.4 | 899.4
47 | 2014-02-14 15:30 | 960.3 | 904.3
48 | 2014-02-14 15:31 | 968.3 | 912.3
49 | 2014-02-14 15:32 | 973.1 | 917.1
50 | 2014-02-14 15:33 | 979.2 | 923.2
51 | 2014-02-14 15:34 | 985.3 | 929.3
52 | 2014-02-14 15:35 | 989.6 | 933.6
53 | 2014-02-14 15:36 | 990.8 | 934.8
54 | 2014-02-14 15:37 | 993.3 | 937.3
55 | 2014-02-14 15:38 | 998.2 | 942.2
56 | 2014-02-14 15:39 | 1001.8 | 945.8
57 | 2014-02-14 15:40 | 1003.1 | 947.1
58 | 2014-02-14 15:41 | 1005.5 | 949.5
59 | 2014-02-14 15:42 | 1001.8 | 945.8
60 | 2014-02-14 15:43 | 1003.1 | 947.1
61 | 2014-02-14 15:44 | 1014 | 958
62 | 2014-02-14 15:45 | 1029.3 | 973.3
63 | 2014-02-14 15:46 | 1037.2 | 981.2
64 | 2014-02-14 15:47 | 1042.1 | 986.1 | 0
65 | 2014-02-14 15:48 | 1040.9 | 984.9 | 0.0020495
66 | 2014-02-14 15:49 | 1037.9 | 981.9 | 0.0071918
67 | 2014-02-14 15:50 | 1015.3 | 959.3 | 0.046804
68 | 2014-02-14 15:51 | 990.2 | 934.2 | 0.09272
69 | 2014-02-14 15:52 | 958.5 | 902.5 | 0.15389
70 | 2014-02-14 15:53 | 937.7 | 881.7 | 0.19617
71 | 2014-02-14 15:54 | 932.8 | 876.8 | 0.20639
72 | 2014-02-14 15:55 | 923.1 | 867.1 | 0.22695
73 | 2014-02-14 15:56 | 917 | 861 | 0.24009
74 | 2014-02-14 15:57 | 907.2 | 851.2 | 0.26158
75 | 2014-02-14 15:58 | 898.7 | 842.7 | 0.2806
76 | 2014-02-14 15:59 | 887.1 | 831.1 | 0.30715
77 | 2014-02-14 16:00 | 881 | 825 | 0.3214
78 | 2014-02-14 16:01 | 862.6 | 806.6 | 0.36566
79 | 2014-02-14 16:02 | 849.8 | 793.8 | 0.39765
80 | 2014-02-14 16:03 | 847.4 | 791.4 | 0.40376
81 | 2014-02-14 16:04 | 835.2 | 779.2 | 0.43543
82 | 2014-02-14 16:05 | 827.8 | 771.8 | 0.45513
83 | 2014-02-14 16:06 | 819.9 | 763.9 | 0.47661
84 | 2014-02-14 16:07 | 809.5 | 753.5 | 0.50561
85 | 2014-02-14 16:08 | 789.4 | 733.4 | 0.56415
86 | 2014-02-14 16:09 | 786.9 | 730.9 | 0.57167
87 | 2014-02-14 16:10 | 777.8 | 721.8 | 0.59956
88 | 2014-02-14 16:11 | 768.6 | 712.6 | 0.62857
89 | 2014-02-14 16:12 | 767.4 | 711.4 | 0.63241
90 | 2014-02-14 16:13 | 765 | 709 | 0.64015
91 | 2014-02-14 16:14 | 768 | 712 | 0.63049
92 | 2014-02-14 16:15 | 816.8 | 760.8 | 0.48517
93 | 2014-02-14 16:16 | 790.6 | 734.6 | 0.56055
94 | 2014-02-14 16:17 | 670.3 | 614.3 | 1.0061
95 | 2014-02-14 16:18 | 583.6 | 527.6 | 1.5246
96 | 2014-02-14 16:19 | 571.4 | 515.4 | 1.6251
97 | 2014-02-14 16:20 | 548.2 | 492.2 | 1.8495
98 | 2014-02-14 16:21 | 520.1 | 464.1 | 2.213
99 | 2014-02-14 16:22 | 514 | 458 | 2.313
100 | 2014-02-14 16:23 | 540.9 | 484.9 | 1.932

## Questions
1) The air exchange rate of the room tested is 1.548 per hour.
2) The ventilation rate in this room is very slow. I would recommend that the occupants leave the room and wait enough time for the chemical to be removed. Since it takes 3/λ hours for the chemical to be removed and our λ is 1.548 per hour, 3/1.548 is 1.94 hours or 2 hours. Since this takes 2 hours to ventilate out, no one should be in the room for those 2 hours.
3) This room could usually fit around 10-15 people. The ventilation rate with 15 people in this room calculates to be 3.82 scfm/person, which is not good. Since the ventilation rate causes only 4 people to be in the room without exceeding the ASHRAE's reccomended rate of 15 scfm/person, we can say that the occupants are just being too cheap to buy a better ventilation system.
4) The maximun number of people that I would recommend to have in this room at one time is 4 people. The ASHRAE ventilation standard is 15 scfm/person and the ventilation rate of this room with 4 people in it is 14.33 scfm/person. Anymore people in this room would cause the ventilation rate to rise above 15 scfm/person.