## load calcs
Calculate the Loads
Load Description | Qty. | Load Current (A) | Load V | AC Load Power (W) | Daily Duty Cycle (hrs/day) | Wkly Duty Cycle | Power Con. Efcy | Nom. Syst. V | Amp-Hour Load (Ah/day)
Criotec | 1 | 3.9 | 117 | 460 | 6 | 7/7=1 | 0.98 | 24 | 117.3469
T8 Lights | 4 | 1.1 | 117 | 128 | 5 | 7/7=1 | 0.98 | 24 | 27.2109
LaLa Leche | 1 | 4.3 | 117 | 498 | 6 | 7/7=1 | 0.98 | 24 | 127.0408
CFL | 1 | 0.21 | 117 | 24 | 4 | 7/7=1 | 0.98 | 24 | 4.0816
Television | 1 | 0.51 | 117 | 60 | 8 | 7/7=1 | 0.98 | 24 | 20.4082
Freezer | 1 | 3.9 | 117 | 460 | 5 | 7/7=1 | 0.98 | 24 | 97.7891
|  | Total Load Power |  | 1630 |  |  | Total Amp-Hour Load |  | 393.8776
Total AC Load Power |  |  | Nominal Syatem V |  | Peak Current Draw |  |  | Kwh load | 9453.0612
1630 |  |  | 24 |  | 67.9167
Total Ah Load |  | Wire Effcy. Factor |  | Battery Effcy. Factor |  | Corrected Ah Load
393.8776 |  | 0.98 |  | 0.9 |  | 446.5732

## current and tilt
Design Current and Array Tilt
System Location | Lattitude | Longitude
Parras | 25.3 | 102.20 W
Tilt at Lat. -15°
Corrected Load (Ah) | Lowest Peak Sun (HRS/DAY) | Design Current (A)
446.5732 | 3.7 | 120.6955
Tilt at Lat.
Corrected Load (Ah) | Lowest Peak Sun (HRS/DAY) | Design Current (A)
446.5732 | 4.2 | 106.3269
Tilt at Lat. +15°
Corrected Load (Ah) | Lowest Peak Sun (HRS/DAY) | Design Current (A)
446.5732 | 4.49 | 99.4595
Flat
Corrected Load (Ah) | Lowest Peak Sun (HRS/DAY) | Design Current (A)
446.5732 | 3.25 | 137.4071
Smallest Design Current (A) |  | Lowest Peak Sun (HRS/DAY) | Tilt Angle
99.4595 |  | 4.49 | 40°

## battery
Calculate System Battery Size
Corrected Ah Load | Storage Days | Max. Depth of Discharge % | Derate for Temp. | Req. Bat. Cap. (Ah) | Cap. of Sel. Bat. (Ah) | Bat. Req. in Parallel
446.5732 | 2 | 0.85 | 0.95 | 1106.0636 | 390 | 2.8361
Nom. Sys. V | Nom. Bat. V | # Batteries in Series | # Bat´s in Parallel | TOTAL Bat´s
24 | 6 | 4 | 3 | 12
Bat´s in Parallel | Cap. Of Sel. Bat. (Ah) | System Bat. Cap. (Ah) | Max. Depth of Discharge (0.##) | Usable Bat. Cap. (Ah)
3 | 390 | 1170 | 0.85 | 994.5
Make | Trojan
Model | L-16P
Type | Deep Cycle
Nom. V | 6
Rated Cap. (Ah) | 390

## array
Calculate System Array Size
Design Current (A) | Module Derate Factor (0.##) | Derated Design Current (A) | Rated Mod. Current (A) | Modules in Parallel
99.4595 | 0.98 | 101.4893 | 4.95 | 20.5029
Safety | Nom. Bat. V | Bat´s in Series | Req´d V for Load | Highest Temp. Mod. V | Mod´s in Series | Mod´s in Parallel | TOTAL Mod´s
1.2 | 6 | 4 | 28.8 | 30 | 1 | 16 | 16
from ret calcs
Mod´s in Parallel | Rated Mod. Current (A) | Rated Array Current (A)
16 | 4.95 | 79.2
| Mod. Short Circuit Current (A) | Array Short Circuit Current (A)
16 | 5.55 | 88.8
Mod´s in Series | Rated Mod. V | Array Rated V
1 | 35.4 | 35.4
| Open Circuit Module V | Array Open Circuit V
1 | 44.4 | 44.4
PV Model Information
Make/Model |  | Nominal Volts
Sharp/ NT-175U1 |  | 24
Length | Width | Thickness
1,575m | 826 mm | 46 mm
Weight | Bypass Diode
17 kg | Yes / No
Voltage | At STC | Open Circuit | At Highest Exp. Temp.
35.4 | 35.4 | 44.4 | 30
Current | At STC | Short Circuit
Current | 4.95 | 5.55

## controller
Controller Specification
Safety | Array Short Circuit Current (A) | Minimum Controller Current (A) | Rated Controller Current (A) | Contollers in Parallel
1.25 | 88.8 | 111 | 60 | 2
Controller Specs
Make/Module | OutBack MX60 MMPT
Rated V | 24V
Rated Current | 60A
Features
Temp. Comp. | yes
MPPT | yes
Reverse Current Prot. | yes
Adjustible Set Points
High V Disconnect | yes
High V Reconn. | yes
Low V Disconnect | yes
Low V Reconn. | yes
Meters
Bat. V | yes
Array Current | yes
Load Current | yes

## inverter
Power Conditioning Unit Specification
INVERTER
System Reqmt´s |  | Inverter Spec´s
Waveform Desired | modified sine | Make/Model | Xantrex DR2424
DC System V --> | 24 | Waveform | modified sine
AC System V --> | 120 | Input DC V | 24
Surge Cap. (W) --> | 6200 | Output AC V | 120
Total AC Watts --> | 1630 | Surge Cap. (W) | 6200
Max. Single AC Load (W) |  | Features
498 |  | Bat. Charging | yes
Max. Simultaneous AC Load (W) |  | Voltometer
1630 |  | Remote Control | optional
Inverter Run Time at Max. Sim. Load (min) |  | Generator Starting
30 |  | Power Transfer Switch
Continuous Duty Rating of Inverter (W) |  | Max. Power Tracking
400
Req´d Inverter Efficiency (%)
95

## dc wiring
DC Wire Sizing Specification
Wire Runs | System V | Max. Current (A) | One-Way Length (ft) | Allowed V Drop (%) | Allowance for Temp. Derate | AWG # | estimated cost/circuit (dollars/ft)
Array Circuit
Mod. to Mod. | 24 | 5.5 | 70 | 3 | + 1 AWG | 11 | 0.91 | 127.4
Array to Controller/Bat. | 24 | 88.8 | 75 | 3 | + 1 AWG | "00" | 2.8 | 420
Branch Circuits
Bat. to Inverter | 24 | 272.7 | 5 | 3 | + 1 AWG | "0000" | 3 | 30
[7 empty] | total ($) | 577.4
Allowance for Temp. Derate
*ambient temperature >90°
+ 1 AWG

## switches
Circuit | Protection Device | Rated Current | Rated Voltage | Description |  | price ($)
Array Output to CC | Switch | 100 amps | 35.4 | DC fused disconnect switch |  | 100
Array Output to CC | Fuse | 100 amps | 35.4 | DC fuse |  | 8
Battery to inverter | Fuse | 70 amps | 24 | DC inline fuse |  | 6
CC to battery | Switch | 100 amps | 24 | DC fused disconnect switch |  | 100
Controller to Inverter | Fuse | 100 amps | 24 | DC fuse |  | 8
[5 empty] | total ($) | 222