## Raw Data
Plot Title: Dorm Room Mason and Pedro Room
# | Date Time, GMT-07:00 | CO2, ppm (LGR S/N: 1273711, SEN S/N: 1273711) | Host Connected (LGR S/N: 1273711) | Stopped (LGR S/N: 1273711) | End Of File (LGR S/N: 1273711)
1 | 2016-10-20 14:46 | 799.8
2 | 2016-10-20 14:47 | 634.9
3 | 2016-10-20 14:48 | 459.1
4 | 2016-10-20 14:49 | 398.7
5 | 2016-10-20 14:50 | 406.6
6 | 2016-10-20 14:51 | 398.7
7 | 2016-10-20 14:52 | 393.8
8 | 2016-10-20 14:53 | 386.4
9 | 2016-10-20 14:54 | 818.1
10 | 2016-10-20 14:55 | 710
11 | 2016-10-20 14:56 | 740.5
12 | 2016-10-20 14:57 | 734.4
13 | 2016-10-20 14:58 | 771.7
14 | 2016-10-20 14:59 | 812.6
15 | 2016-10-20 15:00 | 884
16 | 2016-10-20 15:01 | 950.5
17 | 2016-10-20 15:02 | 1102.6
18 | 2016-10-20 15:03 | 1105.6
19 | 2016-10-20 15:04 | 1129.4
20 | 2016-10-20 15:05 | 1179.5
21 | 2016-10-20 15:06 | 1219.8
22 | 2016-10-20 15:07 | 1239.9
23 | 2016-10-20 15:08 | 1278.4
24 | 2016-10-20 15:09 | 1299.8
25 | 2016-10-20 15:10 | 1366.3
26 | 2016-10-20 15:11 | 1462.8
27 | 2016-10-20 15:12 | 1504.3
28 | 2016-10-20 15:13 | 1570.8
29 | 2016-10-20 15:14 | 1611.1
30 | 2016-10-20 15:15 | 1631.9
31 | 2016-10-20 15:16 | 1656.9
32 | 2016-10-20 15:17 | 1655.7
33 | 2016-10-20 15:18 | 1653.8
34 | 2016-10-20 15:19 | 1647.7
35 | 2016-10-20 15:20 | 1622.7
36 | 2016-10-20 15:21 | 1616
37 | 2016-10-20 15:22 | 1611.7
38 | 2016-10-20 15:23 | 1613.6
39 | 2016-10-20 15:24 | 1602
40 | 2016-10-20 15:25 | 1578.1
41 | 2016-10-20 15:26 | 1565.9
42 | 2016-10-20 15:27 | 1586.1
43 | 2016-10-20 15:28 | 1582.4
44 | 2016-10-20 15:29 | 1579.4
45 | 2016-10-20 15:30 | 1591
46 | 2016-10-20 15:31 | 1594.6
47 | 2016-10-20 15:32 | 1581.2
48 | 2016-10-20 15:33 | 1586.7
49 | 2016-10-20 15:34 | 1590.4
50 | 2016-10-20 15:35 | 1592.2
51 | 2016-10-20 15:36 | 1594.6
52 | 2016-10-20 15:37 | 1603.2
53 | 2016-10-20 15:38 | 1599.5
54 | 2016-10-20 15:39 | 1591.6
55 | 2016-10-20 15:40 | 1553.1
56 | 2016-10-20 15:41 | 1565.9
57 | 2016-10-20 15:42 | 1565.9
58 | 2016-10-20 15:43 | 1561.7
59 | 2016-10-20 15:44 | 1562.9
60 | 2016-10-20 15:45 | 1551.3
61 | 2016-10-20 15:46 | 1500
62 | 2016-10-20 15:47 | 1500.6
63 | 2016-10-20 15:48 | 1503.1
64 | 2016-10-20 15:49 | 1496.9
65 | 2016-10-20 15:50 | 1106.2
66 | 2016-10-20 15:51 | 494.5
67 | 2016-10-20 15:52 | 420
68 | 2016-10-20 15:53 | 441.4
69 | 2016-10-20 15:54 | 437.1
70 | 2016-10-20 15:55 | 426.7
71 | 2016-10-20 15:56 | 401.7
72 | 2016-10-20 15:57 | 418.2
73 | 2016-10-20 15:58 | 556.2
74 | 2016-10-20 15:59 | 523.2
75 | 2016-10-20 15:59 |  | Logged
76 | 2016-10-20 16:00 |  |  | Logged | Logged

## Concentration Analysis
Mason Davidson
ENGR 115
Th 2
2016-10-20
Input Parameters
Measured C outdoor(ppm) | 388
Assumed C outdoor(ppm) | 400
Correction factor(ppm) | 12
Analysis
Measurement | Date and Time | HOBO CO2 Concentrations (ppm) | Actual CO2 Concentration (ppm)
1 | 2016-10-20 14:46 | 799.8 | 811.8
2 | 2016-10-20 14:47 | 634.9 | 646.9
3 | 2016-10-20 14:48 | 459.1 | 471.1
4 | 2016-10-20 14:49 | 398.7 | 410.7
5 | 2016-10-20 14:50 | 406.6 | 418.6
6 | 2016-10-20 14:51 | 398.7 | 410.7
7 | 2016-10-20 14:52 | 393.8 | 405.8
8 | 2016-10-20 14:53 | 386.4 | 398.4
9 | 2016-10-20 14:54 | 818.1 | 830.1
10 | 2016-10-20 14:55 | 710 | 722
11 | 2016-10-20 14:56 | 740.5 | 752.5
12 | 2016-10-20 14:57 | 734.4 | 746.4
13 | 2016-10-20 14:58 | 771.7 | 783.7
14 | 2016-10-20 14:59 | 812.6 | 824.6
15 | 2016-10-20 15:00 | 884 | 896
16 | 2016-10-20 15:01 | 950.5 | 962.5
17 | 2016-10-20 15:02 | 1102.6 | 1114.6
18 | 2016-10-20 15:03 | 1105.6 | 1117.6
19 | 2016-10-20 15:04 | 1129.4 | 1141.4
20 | 2016-10-20 15:05 | 1179.5 | 1191.5
21 | 2016-10-20 15:06 | 1219.8 | 1231.8
22 | 2016-10-20 15:07 | 1239.9 | 1251.9
23 | 2016-10-20 15:08 | 1278.4 | 1290.4
24 | 2016-10-20 15:09 | 1299.8 | 1311.8
25 | 2016-10-20 15:10 | 1366.3 | 1378.3
26 | 2016-10-20 15:11 | 1462.8 | 1474.8
27 | 2016-10-20 15:12 | 1504.3 | 1516.3
28 | 2016-10-20 15:13 | 1570.8 | 1582.8
29 | 2016-10-20 15:14 | 1611.1 | 1623.1
30 | 2016-10-20 15:15 | 1631.9 | 1643.9
31 | 2016-10-20 15:16 | 1656.9 | 1668.9
32 | 2016-10-20 15:17 | 1655.7 | 1667.7
33 | 2016-10-20 15:18 | 1653.8 | 1665.8
34 | 2016-10-20 15:19 | 1647.7 | 1659.7
35 | 2016-10-20 15:20 | 1622.7 | 1634.7
36 | 2016-10-20 15:21 | 1616 | 1628
37 | 2016-10-20 15:22 | 1611.7 | 1623.7
38 | 2016-10-20 15:23 | 1613.6 | 1625.6
39 | 2016-10-20 15:24 | 1602 | 1614
40 | 2016-10-20 15:25 | 1578.1 | 1590.1
41 | 2016-10-20 15:26 | 1565.9 | 1577.9
42 | 2016-10-20 15:27 | 1586.1 | 1598.1
43 | 2016-10-20 15:28 | 1582.4 | 1594.4
44 | 2016-10-20 15:29 | 1579.4 | 1591.4
45 | 2016-10-20 15:30 | 1591 | 1603
46 | 2016-10-20 15:31 | 1594.6 | 1606.6
47 | 2016-10-20 15:32 | 1581.2 | 1593.2
48 | 2016-10-20 15:33 | 1586.7 | 1598.7
49 | 2016-10-20 15:34 | 1590.4 | 1602.4
50 | 2016-10-20 15:35 | 1592.2 | 1604.2
51 | 2016-10-20 15:36 | 1594.6 | 1606.6
52 | 2016-10-20 15:37 | 1603.2 | 1615.2
53 | 2016-10-20 15:38 | 1599.5 | 1611.5
54 | 2016-10-20 15:39 | 1591.6 | 1603.6
55 | 2016-10-20 15:40 | 1553.1 | 1565.1
56 | 2016-10-20 15:41 | 1565.9 | 1577.9
57 | 2016-10-20 15:42 | 1565.9 | 1577.9
58 | 2016-10-20 15:43 | 1561.7 | 1573.7
59 | 2016-10-20 15:44 | 1562.9 | 1574.9
60 | 2016-10-20 15:45 | 1551.3 | 1563.3
61 | 2016-10-20 15:46 | 1500 | 1512
62 | 2016-10-20 15:47 | 1500.6 | 1512.6
63 | 2016-10-20 15:48 | 1503.1 | 1515.1
64 | 2016-10-20 15:49 | 1496.9 | 1508.9
65 | 2016-10-20 15:50 | 1106.2 | 1118.2
66 | 2016-10-20 15:51 | 494.5 | 506.5
67 | 2016-10-20 15:52 | 420 | 432
68 | 2016-10-20 15:53 | 441.4 | 453.4
69 | 2016-10-20 15:54 | 437.1 | 449.1
70 | 2016-10-20 15:55 | 426.7 | 438.7
71 | 2016-10-20 15:56 | 401.7 | 413.7
72 | 2016-10-20 15:57 | 418.2 | 430.2
73 | 2016-10-20 15:58 | 556.2 | 568.2
74 | 2016-10-20 15:59 | 523.2 | 535.2
75 | 2016-10-20 15:59
76 | 2016-10-20 16:00

## Vent Rate Analysis
Mason Davidson
ENGR 115
Th 2
2016-10-20
Input Parameters
Measured C outdoor(ppm) | 388
Assumed C outdoor(ppm) | 400
Correction factor(ppm) | 12
Room Voume (ft^3) | 1287
Room Capacity (people) | 3
Calculations
Air Exchange Rate (1/hr) | 0.2079
Time to remove non Reactive Chemical (hr) | 14.43
Ventilation Rate(ft^3/min/person) | 1.4865
Analysis
Measurement | Date and Time | HOBO CO2 Concentrations (ppm) | Actual CO2 Concentration (ppm) | Experiment Time(hr) | "-LN((Croom(t)-Coutdoor)/(Co-Coutdoor))
0 | 2016-10-20 15:16 | 1656.9 | 1668.9 | 0 | 0
1 | 2016-10-20 15:17 | 1655.7 | 1667.7 | 0.016667 | 0.00094615
2 | 2016-10-20 15:18 | 1653.8 | 1665.8 | 0.033333 | 0.0024461
3 | 2016-10-20 15:19 | 1647.7 | 1659.7 | 0.05 | 0.0072768
4 | 2016-10-20 15:20 | 1622.7 | 1634.7 | 0.066667 | 0.027322
5 | 2016-10-20 15:21 | 1616 | 1628 | 0.083333 | 0.032764
6 | 2016-10-20 15:22 | 1611.7 | 1623.7 | 0.1 | 0.036271
7 | 2016-10-20 15:23 | 1613.6 | 1625.6 | 0.11667 | 0.03472
8 | 2016-10-20 15:24 | 1602 | 1614 | 0.13333 | 0.04423
9 | 2016-10-20 15:25 | 1578.1 | 1590.1 | 0.15 | 0.064113
10 | 2016-10-20 15:26 | 1565.9 | 1577.9 | 0.16667 | 0.074417
11 | 2016-10-20 15:27 | 1586.1 | 1598.1 | 0.18333 | 0.057413
12 | 2016-10-20 15:28 | 1582.4 | 1594.4 | 0.2 | 0.060506
13 | 2016-10-20 15:29 | 1579.4 | 1591.4 | 0.21667 | 0.063021
14 | 2016-10-20 15:30 | 1591 | 1603 | 0.23333 | 0.053332
15 | 2016-10-20 15:31 | 1594.6 | 1606.6 | 0.25 | 0.050344
16 | 2016-10-20 15:32 | 1581.2 | 1593.2 | 0.26667 | 0.061512
17 | 2016-10-20 15:33 | 1586.7 | 1598.7 | 0.28333 | 0.056913
18 | 2016-10-20 15:34 | 1590.4 | 1602.4 | 0.3 | 0.053831
19 | 2016-10-20 15:35 | 1592.2 | 1604.2 | 0.31667 | 0.052335
20 | 2016-10-20 15:36 | 1594.6 | 1606.6 | 0.33333 | 0.050344
21 | 2016-10-20 15:37 | 1603.2 | 1615.2 | 0.35 | 0.043242
22 | 2016-10-20 15:38 | 1599.5 | 1611.5 | 0.36667 | 0.046291
23 | 2016-10-20 15:39 | 1591.6 | 1603.6 | 0.38333 | 0.052833
24 | 2016-10-20 15:40 | 1553.1 | 1565.1 | 0.4 | 0.085343
25 | 2016-10-20 15:41 | 1565.9 | 1577.9 | 0.41667 | 0.074417
26 | 2016-10-20 15:42 | 1565.9 | 1577.9 | 0.43333 | 0.074417
27 | 2016-10-20 15:43 | 1561.7 | 1573.7 | 0.45 | 0.077989
28 | 2016-10-20 15:44 | 1562.9 | 1574.9 | 0.46667 | 0.076967
29 | 2016-10-20 15:45 | 1551.3 | 1563.3 | 0.48333 | 0.08689
30 | 2016-10-20 15:46 | 1500 | 1512 | 0.5 | 0.13199
31 | 2016-10-20 15:47 | 1500.6 | 1512.6 | 0.51667 | 0.13145
32 | 2016-10-20 15:48 | 1503.1 | 1515.1 | 0.53333 | 0.12921
33 | 2016-10-20 15:49 | 1496.9 | 1508.9 | 0.55 | 0.13478
34 | 2016-10-20 15:50 | 1106.2 | 1118.2 | 0.56667 | 0.56916

## Questions
The air exchange rate in my room is .2079
I would recommend that the occupants in my room keep the windows and door open at all times.
The occupants are not supplying enough air because the ventilation rate is 10 times less than what is recommended.
I recommend a maximum occupancy of 1/5 of a person.