## Air Exchange Rate Analysis
Rober Williams
ENGR 115
Thurs 2-5
sept-19-2013
Input Parameters
Measured Coutside [ppm] | 298
Assumed Coutside [ppm] | 400
Correction Factor [ppm] | 102
Room Volume [cubic feet] | 2326
Room Capacity [people] | 25
Calculations:
Air Exchange Rate [per hour] | 1.4746
Time to remove non-reactive chemical [hr] | 2.0345
Ventilation Rate [scf/min/person] | 2.2866
Analysis
Measurement | Date & Time | Hobo CO2 Concentration | CO2 Concentration [ppm]= | Experiment Time [hr] | -ln((Croom-Coutside)/(Co-Coutside))
0 | 2013-09-19 15:42 | 711.2 | 813.2 | 0 | 0
1 | 2013-09-19 15:43 | 696.6 | 798.6 | 0.016667 | 0.035973
2 | 2013-09-19 15:44 | 682.5 | 784.5 | 0.033333 | 0.071988
3 | 2013-09-19 15:45 | 681.3 | 783.3 | 0.05 | 0.075114
4 | 2013-09-19 15:46 | 680.1 | 782.1 | 0.066667 | 0.078249
5 | 2013-09-19 15:47 | 679.5 | 781.5 | 0.083333 | 0.079821
6 | 2013-09-19 15:48 | 679.5 | 781.5 | 0.1 | 0.079821
7 | 2013-09-19 15:49 | 671.6 | 773.6 | 0.11667 | 0.10075
8 | 2013-09-19 15:50 | 671.6 | 773.6 | 0.13333 | 0.10075
9 | 2013-09-19 15:51 | 641 | 743 | 0.15 | 0.1862
10 | 2013-09-19 15:52 | 630 | 732 | 0.16667 | 0.2188
11 | 2013-09-19 15:53 | 622.7 | 724.7 | 0.18333 | 0.24103
12 | 2013-09-19 15:54 | 616 | 718 | 0.2 | 0.26188
13 | 2013-09-19 15:55 | 611.1 | 713.1 | 0.21667 | 0.27741
14 | 2013-09-19 15:56 | 590.4 | 692.4 | 0.23333 | 0.34581
15 | 2013-09-19 15:57 | 581.8 | 683.8 | 0.25 | 0.37566
16 | 2013-09-19 15:58 | 575.7 | 677.7 | 0.26667 | 0.39739
17 | 2013-09-19 15:59 | 565.9 | 667.9 | 0.28333 | 0.43332
18 | 2013-09-19 16:00 | 558.6 | 660.6 | 0.3 | 0.46095
19 | 2013-09-19 16:01 | 556.2 | 658.2 | 0.31667 | 0.4702
20 | 2013-09-19 16:02 | 548.8 | 650.8 | 0.33333 | 0.49928
21 | 2013-09-19 16:03 | 541.5 | 643.5 | 0.35 | 0.52881
22 | 2013-09-19 16:04 | 534.2 | 636.2 | 0.36667 | 0.55925
23 | 2013-09-19 16:05 | 528.1 | 630.1 | 0.38333 | 0.58542
24 | 2013-09-19 16:06 | 522 | 624 | 0.4 | 0.61229
25 | 2013-09-19 16:07 | 512.2 | 614.2 | 0.41667 | 0.65702

## Raw Data
Plot Title: LibraryStudyRoom
# | Date Time, GMT-07:00 | CO2, ppm
1 | 2013-09-19 14:45 | 647.1
2 | 2013-09-19 14:46 | 694.1
3 | 2013-09-19 14:47 | 437.7
4 | 2013-09-19 14:48 | 418.2
5 | 2013-09-19 14:49 | 415.1
6 | 2013-09-19 14:50 | 424.9
7 | 2013-09-19 14:51 | 415.1
8 | 2013-09-19 14:52 | 412.1
9 | 2013-09-19 14:53 | 406
10 | 2013-09-19 14:54 | 398
11 | 2013-09-19 14:55 | 392.6
12 | 2013-09-19 14:56 | 382.2
13 | 2013-09-19 14:57 | 382.8
14 | 2013-09-19 14:58 | 381.6
15 | 2013-09-19 14:59 | 379.7
16 | 2013-09-19 15:00 | 377.3
17 | 2013-09-19 15:01 | 376.7
18 | 2013-09-19 15:02 | 378.5
19 | 2013-09-19 15:03 | 445.1
20 | 2013-09-19 15:04 | 534.2
21 | 2013-09-19 15:05 | 443.8
22 | 2013-09-19 15:06 | 442
23 | 2013-09-19 15:07 | 484.1
24 | 2013-09-19 15:08 | 484.1
25 | 2013-09-19 15:09 | 480.5
26 | 2013-09-19 15:10 | 487.8
27 | 2013-09-19 15:11 | 495.7
28 | 2013-09-19 15:12 | 503.1
29 | 2013-09-19 15:13 | 518.9
30 | 2013-09-19 15:14 | 532.4
31 | 2013-09-19 15:15 | 550.1
32 | 2013-09-19 15:16 | 554.9
33 | 2013-09-19 15:17 | 558
34 | 2013-09-19 15:18 | 570.2
35 | 2013-09-19 15:19 | 583.6
36 | 2013-09-19 15:20 | 598.3
37 | 2013-09-19 15:21 | 603.2
38 | 2013-09-19 15:22 | 608.7
39 | 2013-09-19 15:23 | 614.2
40 | 2013-09-19 15:24 | 617.2
41 | 2013-09-19 15:25 | 622.7
42 | 2013-09-19 15:26 | 630
43 | 2013-09-19 15:27 | 636.8
44 | 2013-09-19 15:28 | 647.1
45 | 2013-09-19 15:29 | 656.9
46 | 2013-09-19 15:30 | 657.5
47 | 2013-09-19 15:31 | 657.5
48 | 2013-09-19 15:32 | 660.6
49 | 2013-09-19 15:33 | 662.4
50 | 2013-09-19 15:34 | 668.5
51 | 2013-09-19 15:35 | 670.3
52 | 2013-09-19 15:36 | 676.4
53 | 2013-09-19 15:37 | 678.3
54 | 2013-09-19 15:38 | 696.6
55 | 2013-09-19 15:39 | 696
56 | 2013-09-19 15:40 | 702.7
57 | 2013-09-19 15:41 | 708.2
58 | 2013-09-19 15:42 | 711.2
59 | 2013-09-19 15:43 | 696.6
60 | 2013-09-19 15:44 | 682.5
61 | 2013-09-19 15:45 | 681.3
62 | 2013-09-19 15:46 | 680.1
63 | 2013-09-19 15:47 | 679.5
64 | 2013-09-19 15:48 | 679.5
65 | 2013-09-19 15:49 | 671.6
66 | 2013-09-19 15:50 | 671.6
67 | 2013-09-19 15:51 | 641
68 | 2013-09-19 15:52 | 630
69 | 2013-09-19 15:53 | 622.7
70 | 2013-09-19 15:54 | 616
71 | 2013-09-19 15:55 | 611.1
72 | 2013-09-19 15:56 | 590.4
73 | 2013-09-19 15:57 | 581.8
74 | 2013-09-19 15:58 | 575.7
75 | 2013-09-19 15:59 | 565.9
76 | 2013-09-19 16:00 | 558.6
77 | 2013-09-19 16:01 | 556.2
78 | 2013-09-19 16:02 | 548.8
79 | 2013-09-19 16:03 | 541.5
80 | 2013-09-19 16:04 | 534.2
81 | 2013-09-19 16:05 | 528.1
82 | 2013-09-19 16:06 | 522
83 | 2013-09-19 16:07 | 512.2
84 | 2013-09-19 16:08 | 509.8
85 | 2013-09-19 16:09 | 511.6
86 | 2013-09-19 16:10 | 514
87 | 2013-09-19 16:11 | 524.4
88 | 2013-09-19 16:12 | 563.5
89 | 2013-09-19 16:13 | 536
90 | 2013-09-19 16:14 | 500.6
91 | 2013-09-19 16:15 | 427.4
92 | 2013-09-19 16:16 | 436.5
93 | 2013-09-19 16:17 | 446.9
94 | 2013-09-19 16:18 | 442

## Concentration Analysis
Rober Williams
ENGR 115
Thurs 2-5
sept-19-2013
Input Parameters
Measured Coutside [ppm] | 298
Assumed Coutside [ppm] | 400
Correction Factor [ppm] | 102
Analysis
Measurement | Date & Time | Hobo CO2 Concentration | CO2 Concentration [ppm]=
1 | 2013-09-19 14:45 | 647.1 | 749.1
2 | 2013-09-19 14:46 | 694.1 | 796.1
3 | 2013-09-19 14:47 | 437.7 | 539.7
4 | 2013-09-19 14:48 | 418.2 | 520.2
5 | 2013-09-19 14:49 | 415.1 | 517.1
6 | 2013-09-19 14:50 | 424.9 | 526.9
7 | 2013-09-19 14:51 | 415.1 | 517.1
8 | 2013-09-19 14:52 | 412.1 | 514.1
9 | 2013-09-19 14:53 | 406 | 508
10 | 2013-09-19 14:54 | 398 | 500
11 | 2013-09-19 14:55 | 392.6 | 494.6
12 | 2013-09-19 14:56 | 382.2 | 484.2
13 | 2013-09-19 14:57 | 382.8 | 484.8
14 | 2013-09-19 14:58 | 381.6 | 483.6
15 | 2013-09-19 14:59 | 379.7 | 481.7
16 | 2013-09-19 15:00 | 377.3 | 479.3
17 | 2013-09-19 15:01 | 376.7 | 478.7
18 | 2013-09-19 15:02 | 378.5 | 480.5
19 | 2013-09-19 15:03 | 445.1 | 547.1
20 | 2013-09-19 15:04 | 534.2 | 636.2
21 | 2013-09-19 15:05 | 443.8 | 545.8
22 | 2013-09-19 15:06 | 442 | 544
23 | 2013-09-19 15:07 | 484.1 | 586.1
24 | 2013-09-19 15:08 | 484.1 | 586.1
25 | 2013-09-19 15:09 | 480.5 | 582.5
26 | 2013-09-19 15:10 | 487.8 | 589.8
27 | 2013-09-19 15:11 | 495.7 | 597.7
28 | 2013-09-19 15:12 | 503.1 | 605.1
29 | 2013-09-19 15:13 | 518.9 | 620.9
30 | 2013-09-19 15:14 | 532.4 | 634.4
31 | 2013-09-19 15:15 | 550.1 | 652.1
32 | 2013-09-19 15:16 | 554.9 | 656.9
33 | 2013-09-19 15:17 | 558 | 660
34 | 2013-09-19 15:18 | 570.2 | 672.2
35 | 2013-09-19 15:19 | 583.6 | 685.6
36 | 2013-09-19 15:20 | 598.3 | 700.3
37 | 2013-09-19 15:21 | 603.2 | 705.2
38 | 2013-09-19 15:22 | 608.7 | 710.7
39 | 2013-09-19 15:23 | 614.2 | 716.2
40 | 2013-09-19 15:24 | 617.2 | 719.2
41 | 2013-09-19 15:25 | 622.7 | 724.7
42 | 2013-09-19 15:26 | 630 | 732
43 | 2013-09-19 15:27 | 636.8 | 738.8
44 | 2013-09-19 15:28 | 647.1 | 749.1
45 | 2013-09-19 15:29 | 656.9 | 758.9
46 | 2013-09-19 15:30 | 657.5 | 759.5
47 | 2013-09-19 15:31 | 657.5 | 759.5
48 | 2013-09-19 15:32 | 660.6 | 762.6
49 | 2013-09-19 15:33 | 662.4 | 764.4
50 | 2013-09-19 15:34 | 668.5 | 770.5
51 | 2013-09-19 15:35 | 670.3 | 772.3
52 | 2013-09-19 15:36 | 676.4 | 778.4
53 | 2013-09-19 15:37 | 678.3 | 780.3
54 | 2013-09-19 15:38 | 696.6 | 798.6
55 | 2013-09-19 15:39 | 696 | 798
56 | 2013-09-19 15:40 | 702.7 | 804.7
57 | 2013-09-19 15:41 | 708.2 | 810.2
58 | 2013-09-19 15:42 | 711.2 | 813.2
59 | 2013-09-19 15:43 | 696.6 | 798.6
60 | 2013-09-19 15:44 | 682.5 | 784.5
61 | 2013-09-19 15:45 | 681.3 | 783.3
62 | 2013-09-19 15:46 | 680.1 | 782.1
63 | 2013-09-19 15:47 | 679.5 | 781.5
64 | 2013-09-19 15:48 | 679.5 | 781.5
65 | 2013-09-19 15:49 | 671.6 | 773.6
66 | 2013-09-19 15:50 | 671.6 | 773.6
67 | 2013-09-19 15:51 | 641 | 743
68 | 2013-09-19 15:52 | 630 | 732
69 | 2013-09-19 15:53 | 622.7 | 724.7
70 | 2013-09-19 15:54 | 616 | 718
71 | 2013-09-19 15:55 | 611.1 | 713.1
72 | 2013-09-19 15:56 | 590.4 | 692.4
73 | 2013-09-19 15:57 | 581.8 | 683.8
74 | 2013-09-19 15:58 | 575.7 | 677.7
75 | 2013-09-19 15:59 | 565.9 | 667.9
76 | 2013-09-19 16:00 | 558.6 | 660.6
77 | 2013-09-19 16:01 | 556.2 | 658.2
78 | 2013-09-19 16:02 | 548.8 | 650.8
79 | 2013-09-19 16:03 | 541.5 | 643.5
80 | 2013-09-19 16:04 | 534.2 | 636.2
81 | 2013-09-19 16:05 | 528.1 | 630.1
82 | 2013-09-19 16:06 | 522 | 624
83 | 2013-09-19 16:07 | 512.2 | 614.2
84 | 2013-09-19 16:08 | 509.8 | 611.8
85 | 2013-09-19 16:09 | 511.6 | 613.6
86 | 2013-09-19 16:10 | 514 | 616
87 | 2013-09-19 16:11 | 524.4 | 626.4
88 | 2013-09-19 16:12 | 563.5 | 665.5
89 | 2013-09-19 16:13 | 536 | 638
90 | 2013-09-19 16:14 | 500.6 | 602.6
91 | 2013-09-19 16:15 | 427.4 | 529.4
92 | 2013-09-19 16:16 | 436.5 | 538.5
93 | 2013-09-19 16:17 | 446.9 | 548.9
94 | 2013-09-19 16:18 | 442 | 544